## 2023 ZAR Existing Plants
| Apr 2023 Deflator | 1.4764
Eskom coal fleet | Plant/Technology | Installed Capacity |  |  | Source | Efficiency | Source | Variable Cost |  | Source | Fixed Cost |  | Source | Annual Availability |  | Source | Overnight cost |  |  |  |  | Source
|  | GW | GW | GW |  | % |  | R/GJ | R/kW |  | % |  |  | % |  |  | R/kW | R/kW | R/kW | R/kW | R/kW
|  | 2020 | 2021 | 2022 | [6 empty] | 2020 | 2025 |  | 2030 | 2035 |  | 2020 | 2025 | 2030 | 2035 | 2050
| Arnot | 2.232 | 2.232 | 2.232 |  | 31% |  | 13.5827 | 564.2737 |  | 55% | 48% |  | - | - |  | - | - | - | - | -
| Camden | 1.45 | 1.45 | 1.45 |  | 28% |  | 13.5827 | 564.2737 |  | 50% |  |  | - | - |  | - | - | - | - | -
| Duvha | 2.875 | 2.875 | 2.875 |  | 33% |  | 13.5827 | 564.2737 |  | 46% | 45% |  | 41% | 41% |  | - | - | - | - | -
| Grootvlei | 0.54 | 0.54 | 0.54 |  | 26% |  | 13.5827 | 564.2737 |  | 75% | 40% |  | - | - |  | - | - | - | - | -
| Hendrina | 1.293 | 1.1083 | 1.1083 |  | 27% |  | 13.5827 | 564.2737 |  | 51% |  |  | - | - |  | - | - | - | - | -
| Kendal | 3.84 | 3.84 | 3.84 |  | 32% |  | 13.5827 | 564.2737 |  | 64% | 64% |  | 61% | 61% |  | - | - | - | - | -
| Komati | 0.092 | 0 | 0 |  | 24% |  | 13.5827 | 564.2737 |  | 73% |  |  | - | - |  | - | - | - | - | -
| Kriel | 2.85 | 2.85 | 2.85 |  | 31% |  | 13.5827 | 564.2737 |  | 45% | 47% |  | - | - |  | - | - | - | - | -
| Kusile | 2.133 | 2.133 | 2.133 |  | 37% |  | 13.5827 | 564.2737 |  | 66% | 72% |  | 67% | 80% |  | - | - | - | - | -
| Lethabo | 3.558 | 3.558 | 3.558 |  | 34% |  | 13.5827 | 564.2737 |  | 62% | 55% |  | 50% | 50% |  | - | - | - | - | -
| Majuba wet cooled | 2.01 | 2.01 | 2.01 |  | 31% |  | 13.5827 | 564.2737 |  | 67% | 67% |  | 59% | 59% |  | - | - | - | - | -
| Majuba dry cooled | 1.833 | 1.833 | 1.833 |  | 30% |  | 13.5827 | 564.2737 |  | 67% | 67% |  | 59% | 59% |  | - | - | - | - | -
| Matimba | 3.69 | 3.69 | 3.69 |  | 34% |  | 13.5827 | 564.2737 |  | 83% | 78% |  | 79% | 79% |  | - | - | - | - | -
| Matla | 3.45 | 3.45 | 3.45 |  | 33% |  | 13.5827 | 564.2737 |  | 62% | 61% |  | 58% | 58% |  | - | - | - | - | -
| Medupi | 3.61 | 3.61 | 3.61 |  | 37% |  | 13.5827 | 564.2737 |  | 70% | 71% |  | 68% | 80% |  | - | - | - | - | -
| Tutuka | 3.51 | 3.51 | 3.51 |  | 31% |  | 13.5827 | 564.2737 |  | 47% | 45% |  | - | - |  | - | - | - | - | -
Other Exisiting Plants | Kelvin coal plant | 0.6 | 0.6 | 0.6 |  | 25% |  | 13.5827 | 564.2737 |  | 32% | 32% |  | 32% | 32% |  | - | - | - | - | -
| Sasol SSF Coal Plant | 0.333 | 0.3 | 0.2667 |  | 25% |  | 13.5827 | 564.2737 |  | 73% | 73% |  | 73% | 73% |  | - | - | - | - | -
| Sasol Infrachem Coal Plant | 0.128 | 0.128 | 0.128 |  | 25% |  | 13.5827 | 564.2737 |  | 56% | 56% |  | 56% | 56% |  | - | - | - | - | -
| Sasol SSF Gas Plant | 0.249 | 0.249 | 0.249 |  | 33% |  | 1.0335 | 238.7312 |  | 85% | 85% |  | 85% | 85% |  | - | - | - | - | -
| Sasol Infrachem Gas Plant | 0.172 | 0.172 | 0.172 |  | 45% |  | 28.9371 | 627.7582 |  | 85% | 85% |  | 85% | 85% |  | - | - | - | - | -
| Eskom OCGT | 2.4 | 2.4 | 2.4 |  | 32% |  | 0 | 98.1795 |  | 96% | 96% |  | 96% | 96% |  | - | - | - | - | -
| IPP OCGT | 1.005 | 1.005 | 1.005 |  | 31% |  | 1.0335 | 238.7312 |  | 80% | 80% |  | 80% | 80% |  | - | - | - | - | -
| Hydro South Africa | 0.665 | 0.665 | 0.665 |  | 100% |  | 0 | 61.1223 |  | 12% | 12% |  | 12% | 12% |  | - | - | - | - | -
| Hydro Cahora Bassa | 1.5 | 1.5 | 1.5 |  | 0% |  | 139.3706 | 61.1223 |  | 69% | 69% |  | 69% | 69% |  | - | - | - | - | -
| Drakensberg / Palmiet pumped storage | 1.58 | 1.58 | 1.58 |  | 73% |  | 0 | 6.6437 |  | 100% | 100% |  | 100% | 100% |  | - | - | - | - | -
| Ingula pumped storage | 1.32 | 1.32 | 1.32 |  | 78% |  | 0 | 270.3258 |  | 66% | 66% |  | 66% | 66% |  | - | - | - | - | -
| Koeberg nuclear | 1.86 | 1.86 | 1.86 |  | 32% |  | 0 | 590.9962 |  | 93% | 93% |  | 93% | 93% |  | - | - | - | - | -
Source: JETP-IP Secretariat, 2022
Apr 2023 Deflator: (see Deflator sheet) | 1.4764
Variable costs EXCLUDE fuel costs and are measured on plant output.

## 2023 ZAR New Capacity Option
April 2023 ZAR
New Capacity Options | Plant/Technology | Installed Capacity |  |  | Source | Efficiency | Source | Variable Cost |  | Source | Fixed Cost |  | Source | Annual Availability |  | Source | Overnight cost |  |  |  |  | Source
|  | GW | GW | GW |  | % |  | R/GJ | R/kW |  | % |  |  | % |  |  | R/kW | R/kW | R/kW | R/kW | R/kW
|  | 2020 | 2021 | 2022 | [6 empty] | 2020 | 2025 |  | 2030 | 2035 |  | 2020 | 2025 | 2030 | 2035 | 2050
| Generic Waterberg Coal Plant | – | – | – |  | 44% |  | 33.071 | 1376.875 |  | 80% | 80% |  | 80% | 80% |  | 58073.5358 | 58073.5358 | 58073.5358 | 58073.5358 | 58073.5358
| Generic Waterberg Coal Plant with CCS | – | – | – |  | 33% |  | 60.9746 | 2347.4494 |  | 80% | 80% |  | 80% | 80% |  | 112333.5735 | 112333.5735 | 112333.5735 | 112333.5735 | 112333.5735
| Fluidised Bed Combustion Coal | – | – | – |  | 36% |  | 71.6046 | 925.8399 |  | 80% | 80% |  | 80% | 80% |  | 70095.7247 | 70095.7247 | 70095.7247 | 70095.7247 | 70095.7247
| Open Cycle Gas Turbine – LNG | – | – | – |  | 31% |  | 1.0335 | 238.7312 |  | 85% | 85% |  | 85% | 85% |  | 13384.8907 | 13384.8907 | 13384.8907 | 13384.8907 | 13384.8907
| Combined Cycle Gas Turbine – LNG | – | – | – |  | 49% |  | 9.0059 | 246.556 |  | 85% | 85% |  | 85% | 85% |  | 14697.3954 | 14697.3954 | 14697.3954 | 14697.3954 | 14697.3954
| Combined Cycle Gas Turbine – LNG-CCS | – | – | – |  | 41% |  | 14.0256 | 585.5336 |  | 85% | 85% |  | 85% | 85% |  | 32295.8839 | 32295.8839 | 32295.8839 | 32295.8839 | 32295.8839
| Gas Engines – LNG | – | – | – |  | 45% |  | 28.9371 | 627.7582 |  | 85% | 85% |  | 85% | 85% |  | 20881.9649 | 20881.9649 | 20881.9649 | 20881.9649 | 20881.9649
| Hydrogen Turbine or Fuel Cell | – | – | – |  | 50% |  | 110.1382 | 0 |  | 85% | 85% |  | 85% | 85% |  | 34706.8178 | 34706.8178 | 34706.8178 | 34706.8178 | 34706.8178
| Biomass municipal waste | – | – | – |  | 45% |  | 47.2443 | 2354.0931 |  | 85% | 85% |  | 85% | 85% |  | 27919.8839 | 27919.8839 | 27919.8839 | 27919.8839 | 27919.8839
| Landfill gas | – | – | – |  | 45% |  | 25.5414 | 2354.0931 |  | 85% | 85% |  | 85% | 85% |  | 27919.8839 | 27919.8839 | 27919.8839 | 27919.8839 | 27919.8839
| New Nuclear | – | – | – |  | 35% |  | 15.3544 | 1442.1312 |  | 85% | 85% |  | 85% | 85% |  | 101206.0729 | 101206.0729 | 101206.0729 | 101206.0729 | 101206.0729
| Wind | 1.937 | 2.353 | 2.881 |  | 100% |  | 0 | 902.0702 |  | 35% | 35% |  | 35% | 35% |  | 18454.7908 | 18293.865 | 18134.4157 | 17818.4696 | 17508.4291
| Solar Central Receiver 9 hrs storage | 0.5 | 0.5 | 0.5 |  | 100% |  | 0.29528 | 1501.4818 |  | 47% | 47% |  | 47% | 47% |  | 77703.5277 | 64959.3873 | 52216.7233 | 52216.7233 | 52216.7233
| Solar PV Fixed | 0.774 | 0.774 | 0.774 |  | 100% |  | 0 | 398.3282 |  | 25% | 25% |  | 25% | 25% |  | 14501.0364 | 13612.2537 | 12788.4318 | 11360.7692 | 10036.4534
| Solar PV tracking | 0.494 | 1.177 | 1.232 |  | 100% |  | 0 | 421.9503 |  | 28% | 28% |  | 28% | 28% |  | 15459.2092 | 14511.3711 | 13632.9231 | 12110.7719 | 10699.3495
| Solar PV rooftop commercial | 0.9522 | 1.2322 | 1.2322 |  | 100% |  | 0 | 461.9603 |  | 20% | 20% |  | 20% | 20% |  | 16821.9109 | 15789.919 | 14834.6991 | 13178.197 | 11642.7584
| Solar PV rooftop residential | 0.1234 | 0.1634 | 0.1634 |  | 100% |  | 0 | 697.0005 |  | 20% | 20% |  | 20% | 20% |  | 25377.552 | 23821.444 | 22379.0175 | 19880.9771 | 17564.5317
| Solar PV rooftop Industry | 0.1584 | 0.2384 | 0.2384 |  | 100% |  | 0 | 461.9603 |  | 20% | 20% |  | 20% | 20% |  | 16821.9109 | 15789.919 | 14834.6991 | 13178.197 | 11642.7584
| Grand Inga | – | – | – |  | 100% |  | 0 | 0 |  | 78% | 78% |  | 78% | 78% |  | 75630.6856 | 75630.6856 | 75630.6856 | 75630.6856 | 75630.6856
| Utility scale battery storage – 4hrs | – | – | – |  | 89% |  | 0 | 919.1962 |  | 85% | 85% |  | 85% | 85% |  | 24375.0877 | 16824.8637 | 13694.9312 | 11982.3266 | 10271.1984
Apr 2023 Deflator: (see Deflator sheet) | 1.4764

## IRP 2023
Technology | Parameter | Currency reference | Units | Source | Description | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
Wind | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | Wind | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657
Wind | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | Wind | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955
Wind | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | Wind | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762
Wind | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | Wind | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3%
Wind | WACC | Apr-23 ZAR | % | IRP 2023 | Wind | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
Wind | Lifetime |  | years | EPRI 2021 | Wind | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Wind | Capital recovery factor |  | % | Calculated | Wind | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528%
Wind | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | Wind | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161
Wind | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | Wind | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687
Solar PV tracking | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | PV Thin Film CDTe (SAT) | 24472 | 24472 | 24472 | 24472 | 24472 | 24472 | 24472 | 24472 | 24472 | 24472 | 24472 | 24472 | 24472 | 24472 | 24472 | 24472 | 24472 | 24472 | 24472 | 24472 | 24472 | 24472 | 24472 | 24472 | 24472 | 24472 | 24472 | 24472
Solar PV tracking | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | PV Thin Film CDTe (SAT) | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295
Solar PV tracking | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | PV Thin Film CDTe (SAT) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar PV tracking | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | PV Thin Film CDTe (SAT) | 25206.16 | 25206.16 | 25206.16 | 25206.16 | 25206.16 | 25206.16 | 25206.16 | 25206.16 | 25206.16 | 25206.16 | 25206.16 | 25206.16 | 25206.16 | 25206.16 | 25206.16 | 25206.16 | 25206.16 | 25206.16 | 25206.16 | 25206.16 | 25206.16 | 25206.16 | 25206.16 | 25206.16 | 25206.16 | 25206.16 | 25206.16 | 25206.16
Solar PV tracking | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | PV Thin Film CDTe (SAT) | 26.5% | 26.5% | 26.5% | 26.5% | 26.5% | 26.5% | 26.5% | 26.5% | 26.5% | 26.5% | 26.5% | 26.5% | 26.5% | 26.5% | 26.5% | 26.5% | 26.5% | 26.5% | 26.5% | 26.5% | 26.5% | 26.5% | 26.5% | 26.5% | 26.5% | 26.5% | 26.5% | 26.5%
Solar PV tracking | WACC | Apr-23 ZAR | years | IRP 2023 | PV Thin Film CDTe (SAT) | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
Solar PV tracking | Lifetime |  | years | EPRI 2021 | PV Thin Film CDTe (SAT) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Solar PV tracking | Capital recovery factor |  | % | Calculated | PV Thin Film CDTe (SAT) | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528%
Solar PV tracking | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | PV Thin Film CDTe (SAT) | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523 | 2696.7523
Solar PV tracking | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | PV Thin Film CDTe (SAT) | 1.1617 | 1.1617 | 1.1617 | 1.1617 | 1.1617 | 1.1617 | 1.1617 | 1.1617 | 1.1617 | 1.1617 | 1.1617 | 1.1617 | 1.1617 | 1.1617 | 1.1617 | 1.1617 | 1.1617 | 1.1617 | 1.1617 | 1.1617 | 1.1617 | 1.1617 | 1.1617 | 1.1617 | 1.1617 | 1.1617 | 1.1617 | 1.1617
Battery storage 4h -1 | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | BESS 4h | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557
Battery storage 4h -1 | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | BESS 4h | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185
Battery storage 4h -1 | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | BESS 4h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery storage 4h -1 | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | BESS 4h | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557 | 37557
Battery storage 4h -1 | WACC | Apr-23 ZAR | % | IRP 2023 | BESS 4h | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
Battery storage 4h -1 | Lifetime | Apr-23 ZAR | years | EPRI 2021 | BESS 4h | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Battery storage 4h -1 | Capital recovery factor |  | % | Calculated | BESS 4h | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34%
Battery storage 4h -1 | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | BESS 4h | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714 | 5067.3714
Battery storage 4h -2 | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | BESS 4h | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216
Battery storage 4h -2 | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | BESS 4h | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185 | 1185
Battery storage 4h -2 | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | BESS 4h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery storage 4h -2 | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | BESS 4h | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216 | 35216
Battery storage 4h -2 | WACC | Apr-23 ZAR | % | IRP 2023 | BESS 4h | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
Battery storage 4h -2 | Lifetime | Apr-23 ZAR | years | EPRI 2021 | BESS 4h | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Battery storage 4h -2 | Capital recovery factor |  |  | Calculated | BESS 4h | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34%
Battery storage 4h -2 | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | BESS 4h | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757 | 4825.3757
Battery storage 1h -1 | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | BESS 1h | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818
Battery storage 1h -1 | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | BESS 1h | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382
Battery storage 1h -1 | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | BESS 1h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery storage 1h -1 | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | BESS 1h | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818 | 20818
Battery storage 1h -1 | WACC | Apr-23 ZAR | % | IRP 2023 | BESS 1h | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
Battery storage 1h -1 | Lifetime | Apr-23 ZAR | years | EPRI 2021 | BESS 1h | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Battery storage 1h -1 | Capital recovery factor |  | % | Calculated | BESS 1h | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34%
Battery storage 1h -1 | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | BESS 1h | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145 | 2534.0145
Battery storage 1h -2 | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | BESS 1h | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615
Battery storage 1h -2 | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | BESS 1h | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382 | 382
Battery storage 1h -2 | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | BESS 1h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery storage 1h -2 | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | BESS 1h | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615 | 15615
Battery storage 1h -2 | WACC | Apr-23 ZAR | % | IRP 2023 | BESS 1h | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
Battery storage 1h -2 | Lifetime | Apr-23 ZAR | years | EPRI 2021 | BESS 1h | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Battery storage 1h -2 | Capital recovery factor |  | % | Calculated | BESS 1h | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34% | 10.34%
Battery storage 1h -2 | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | BESS 1h | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659 | 1996.1659
PHS | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | PHS | 25500.06 | 25500.06 | 25500.06 | 25500.06 | 25500.06 | 25500.06 | 25500.06 | 25500.06 | 25500.06 | 25500.06 | 25500.06 | 25500.06 | 25500.06 | 25500.06 | 25500.06 | 25500.06 | 25500.06 | 25500.06 | 25500.06 | 25500.06 | 25500.06 | 25500.06 | 25500.06 | 25500.06 | 25500.06 | 25500.06 | 25500.06 | 25500.06
PHS | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | PHS | 327.16 | 327.16 | 327.16 | 327.16 | 327.16 | 327.16 | 327.16 | 327.16 | 327.16 | 327.16 | 327.16 | 327.16 | 327.16 | 327.16 | 327.16 | 327.16 | 327.16 | 327.16 | 327.16 | 327.16 | 327.16 | 327.16 | 327.16 | 327.16 | 327.16 | 327.16 | 327.16 | 327.16
PHS | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | PHS | 544.73 | 544.73 | 544.73 | 544.73 | 544.73 | 544.73 | 544.73 | 544.73 | 544.73 | 544.73 | 544.73 | 544.73 | 544.73 | 544.73 | 544.73 | 544.73 | 544.73 | 544.73 | 544.73 | 544.73 | 544.73 | 544.73 | 544.73 | 544.73 | 544.73 | 544.73 | 544.73 | 544.73
PHS | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | PHS | 31799.984 | 31799.984 | 31799.984 | 31799.984 | 31799.984 | 31799.984 | 31799.984 | 31799.984 | 31799.984 | 31799.984 | 31799.984 | 31799.984 | 31799.984 | 31799.984 | 31799.984 | 31799.984 | 31799.984 | 31799.984 | 31799.984 | 31799.984 | 31799.984 | 31799.984 | 31799.984 | 31799.984 | 31799.984 | 31799.984 | 31799.984 | 31799.984
PHS | WACC | Apr-23 ZAR | % | IRP 2023 | PHS | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
PHS | Lifetime | Apr-23 ZAR | years | Meridian 2020 | PHS | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
PHS | Capital recovery factor |  | % | Calculated | PHS | 8.363% | 8.363% | 8.363% | 8.363% | 8.363% | 8.363% | 8.363% | 8.363% | 8.363% | 8.363% | 8.363% | 8.363% | 8.363% | 8.363% | 8.363% | 8.363% | 8.363% | 8.363% | 8.363% | 8.363% | 8.363% | 8.363% | 8.363% | 8.363% | 8.363% | 8.363% | 8.363% | 8.363%
PHS | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | PHS | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482 | 2986.4482
CSP trough 3hrs | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | CSP trough 3hrs | 119365 | 119365 | 119365 | 119365 | 119365 | 119365 | 119365 | 119365 | 119365 | 119365 | 119365 | 119365 | 119365 | 119365 | 119365 | 119365 | 119365 | 119365 | 119365 | 119365 | 119365 | 119365 | 119365 | 119365 | 119365 | 119365 | 119365 | 119365
CSP trough 3hrs | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | CSP trough 3hrs | 977 | 977 | 977 | 977 | 977 | 977 | 977 | 977 | 977 | 977 | 977 | 977 | 977 | 977 | 977 | 977 | 977 | 977 | 977 | 977 | 977 | 977 | 977 | 977 | 977 | 977 | 977 | 977
CSP trough 3hrs | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | CSP trough 3hrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CSP trough 3hrs | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | CSP trough 3hrs | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295 | 132047.9295
CSP trough 3hrs | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | CSP trough 3hrs | 32.5% | 32.5% | 32.5% | 32.5% | 32.5% | 32.5% | 32.5% | 32.5% | 32.5% | 32.5% | 32.5% | 32.5% | 32.5% | 32.5% | 32.5% | 32.5% | 32.5% | 32.5% | 32.5% | 32.5% | 32.5% | 32.5% | 32.5% | 32.5% | 32.5% | 32.5% | 32.5% | 32.5%
CSP trough 3hrs | WACC | Apr-23 ZAR | years | IRP 2023 | CSP trough 3hrs | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
CSP trough 3hrs | Lifetime |  | years | EPRI 2021 | CSP trough 3hrs | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
CSP trough 3hrs | Capital recovery factor |  | % | Calculated | CSP trough 3hrs | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051%
CSP trough 3hrs | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | CSP trough 3hrs | 12928.513 | 12928.513 | 12928.513 | 12928.513 | 12928.513 | 12928.513 | 12928.513 | 12928.513 | 12928.513 | 12928.513 | 12928.513 | 12928.513 | 12928.513 | 12928.513 | 12928.513 | 12928.513 | 12928.513 | 12928.513 | 12928.513 | 12928.513 | 12928.513 | 12928.513 | 12928.513 | 12928.513 | 12928.513 | 12928.513 | 12928.513 | 12928.513
CSP trough 3hrs | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | CSP trough 3hrs | 4.5411 | 4.5411 | 4.5411 | 4.5411 | 4.5411 | 4.5411 | 4.5411 | 4.5411 | 4.5411 | 4.5411 | 4.5411 | 4.5411 | 4.5411 | 4.5411 | 4.5411 | 4.5411 | 4.5411 | 4.5411 | 4.5411 | 4.5411 | 4.5411 | 4.5411 | 4.5411 | 4.5411 | 4.5411 | 4.5411 | 4.5411 | 4.5411
CSP trough 6hrs | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | CSP trough 6hrs | 146086 | 146086 | 146086 | 146086 | 146086 | 146086 | 146086 | 146086 | 146086 | 146086 | 146086 | 146086 | 146086 | 146086 | 146086 | 146086 | 146086 | 146086 | 146086 | 146086 | 146086 | 146086 | 146086 | 146086 | 146086 | 146086 | 146086 | 146086
CSP trough 6hrs | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | CSP trough 6hrs | 1003 | 1003 | 1003 | 1003 | 1003 | 1003 | 1003 | 1003 | 1003 | 1003 | 1003 | 1003 | 1003 | 1003 | 1003 | 1003 | 1003 | 1003 | 1003 | 1003 | 1003 | 1003 | 1003 | 1003 | 1003 | 1003 | 1003 | 1003
CSP trough 6hrs | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | CSP trough 6hrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CSP trough 6hrs | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | CSP trough 6hrs | 161608.125 | 161608.125 | 161608.125 | 161608.125 | 161608.125 | 161608.125 | 161608.125 | 161608.125 | 161608.125 | 161608.125 | 161608.125 | 161608.125 | 161608.125 | 161608.125 | 161608.125 | 161608.125 | 161608.125 | 161608.125 | 161608.125 | 161608.125 | 161608.125 | 161608.125 | 161608.125 | 161608.125 | 161608.125 | 161608.125 | 161608.125 | 161608.125
CSP trough 6hrs | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | CSP trough 6hrs | 38% | 38% | 38% | 38% | 38% | 38% | 38% | 38% | 38% | 38% | 38% | 38% | 38% | 38% | 38% | 38% | 38% | 38% | 38% | 38% | 38% | 38% | 38% | 38% | 38% | 38% | 38% | 38%
CSP trough 6hrs | WACC | Apr-23 ZAR | years | IRP 2023 | CSP trough 6hrs | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
CSP trough 6hrs | Lifetime |  | years | EPRI 2021 | CSP trough 6hrs | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
CSP trough 6hrs | Capital recovery factor |  | % | Calculated | CSP trough 6hrs | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051%
CSP trough 6hrs | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | CSP trough 6hrs | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738 | 15629.9738
CSP trough 6hrs | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | CSP trough 6hrs | 4.6954 | 4.6954 | 4.6954 | 4.6954 | 4.6954 | 4.6954 | 4.6954 | 4.6954 | 4.6954 | 4.6954 | 4.6954 | 4.6954 | 4.6954 | 4.6954 | 4.6954 | 4.6954 | 4.6954 | 4.6954 | 4.6954 | 4.6954 | 4.6954 | 4.6954 | 4.6954 | 4.6954 | 4.6954 | 4.6954 | 4.6954 | 4.6954
CSP trough 9hrs | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | CSP trough 9hrs | 177881 | 177881 | 177881 | 177881 | 177881 | 177881 | 177881 | 177881 | 177881 | 177881 | 177881 | 177881 | 177881 | 177881 | 177881 | 177881 | 177881 | 177881 | 177881 | 177881 | 177881 | 177881 | 177881 | 177881 | 177881 | 177881 | 177881 | 177881
CSP trough 9hrs | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | CSP trough 9hrs | 1027 | 1027 | 1027 | 1027 | 1027 | 1027 | 1027 | 1027 | 1027 | 1027 | 1027 | 1027 | 1027 | 1027 | 1027 | 1027 | 1027 | 1027 | 1027 | 1027 | 1027 | 1027 | 1027 | 1027 | 1027 | 1027 | 1027 | 1027
CSP trough 9hrs | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | CSP trough 9hrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CSP trough 9hrs | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | CSP trough 9hrs | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498 | 196781.4498
CSP trough 9hrs | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | CSP trough 9hrs | 45.6% | 45.6% | 45.6% | 45.6% | 45.6% | 45.6% | 45.6% | 45.6% | 45.6% | 45.6% | 45.6% | 45.6% | 45.6% | 45.6% | 45.6% | 45.6% | 45.6% | 45.6% | 45.6% | 45.6% | 45.6% | 45.6% | 45.6% | 45.6% | 45.6% | 45.6% | 45.6% | 45.6%
CSP trough 9hrs | WACC | Apr-23 ZAR | years | IRP 2023 | CSP trough 9hrs | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
CSP trough 9hrs | Lifetime |  | years | EPRI 2021 | CSP trough 9hrs | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
CSP trough 9hrs | Capital recovery factor |  | % | Calculated | CSP trough 9hrs | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051%
CSP trough 9hrs | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | CSP trough 9hrs | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727 | 18837.4727
CSP trough 9hrs | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | CSP trough 9hrs | 4.7158 | 4.7158 | 4.7158 | 4.7158 | 4.7158 | 4.7158 | 4.7158 | 4.7158 | 4.7158 | 4.7158 | 4.7158 | 4.7158 | 4.7158 | 4.7158 | 4.7158 | 4.7158 | 4.7158 | 4.7158 | 4.7158 | 4.7158 | 4.7158 | 4.7158 | 4.7158 | 4.7158 | 4.7158 | 4.7158 | 4.7158 | 4.7158
CSP tower 3hrs | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | CSP tower 3hrs | 114936 | 114936 | 114936 | 114936 | 114936 | 114936 | 114936 | 114936 | 114936 | 114936 | 114936 | 114936 | 114936 | 114936 | 114936 | 114936 | 114936 | 114936 | 114936 | 114936 | 114936 | 114936 | 114936 | 114936 | 114936 | 114936 | 114936 | 114936
CSP tower 3hrs | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | CSP tower 3hrs | 898 | 898 | 898 | 898 | 898 | 898 | 898 | 898 | 898 | 898 | 898 | 898 | 898 | 898 | 898 | 898 | 898 | 898 | 898 | 898 | 898 | 898 | 898 | 898 | 898 | 898 | 898 | 898
CSP tower 3hrs | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | CSP tower 3hrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CSP tower 3hrs | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | CSP tower 3hrs | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335 | 127148.3335
CSP tower 3hrs | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | CSP tower 3hrs | 39.5% | 39.5% | 39.5% | 39.5% | 39.5% | 39.5% | 39.5% | 39.5% | 39.5% | 39.5% | 39.5% | 39.5% | 39.5% | 39.5% | 39.5% | 39.5% | 39.5% | 39.5% | 39.5% | 39.5% | 39.5% | 39.5% | 39.5% | 39.5% | 39.5% | 39.5% | 39.5% | 39.5%
CSP tower 3hrs | WACC | Apr-23 ZAR | years | IRP 2023 | CSP tower 3hrs | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
CSP tower 3hrs | Lifetime |  | years | EPRI 2021 | CSP tower 3hrs | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
CSP tower 3hrs | Capital recovery factor |  | % | Calculated | CSP tower 3hrs | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051%
CSP tower 3hrs | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | CSP tower 3hrs | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559 | 12406.0559
CSP tower 3hrs | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | CSP tower 3hrs | 3.5854 | 3.5854 | 3.5854 | 3.5854 | 3.5854 | 3.5854 | 3.5854 | 3.5854 | 3.5854 | 3.5854 | 3.5854 | 3.5854 | 3.5854 | 3.5854 | 3.5854 | 3.5854 | 3.5854 | 3.5854 | 3.5854 | 3.5854 | 3.5854 | 3.5854 | 3.5854 | 3.5854 | 3.5854 | 3.5854 | 3.5854 | 3.5854
CSP tower 6hrs | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | CSP tower 6hrs | 139324 | 139324 | 139324 | 139324 | 139324 | 139324 | 139324 | 139324 | 139324 | 139324 | 139324 | 139324 | 139324 | 139324 | 139324 | 139324 | 139324 | 139324 | 139324 | 139324 | 139324 | 139324 | 139324 | 139324 | 139324 | 139324 | 139324 | 139324
CSP tower 6hrs | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | CSP tower 6hrs | 938 | 938 | 938 | 938 | 938 | 938 | 938 | 938 | 938 | 938 | 938 | 938 | 938 | 938 | 938 | 938 | 938 | 938 | 938 | 938 | 938 | 938 | 938 | 938 | 938 | 938 | 938 | 938
CSP tower 6hrs | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | CSP tower 6hrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CSP tower 6hrs | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | CSP tower 6hrs | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399 | 154127.6399
CSP tower 6hrs | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | CSP tower 6hrs | 51% | 51% | 51% | 51% | 51% | 51% | 51% | 51% | 51% | 51% | 51% | 51% | 51% | 51% | 51% | 51% | 51% | 51% | 51% | 51% | 51% | 51% | 51% | 51% | 51% | 51% | 51% | 51%
CSP tower 6hrs | WACC | Apr-23 ZAR | years | IRP 2023 | CSP tower 6hrs | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
CSP tower 6hrs | Lifetime |  | years | EPRI 2021 | CSP tower 6hrs | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
CSP tower 6hrs | Capital recovery factor |  | % | Calculated | CSP tower 6hrs | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051%
CSP tower 6hrs | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | CSP tower 6hrs | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233 | 14887.9233
CSP tower 6hrs | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | CSP tower 6hrs | 3.3324 | 3.3324 | 3.3324 | 3.3324 | 3.3324 | 3.3324 | 3.3324 | 3.3324 | 3.3324 | 3.3324 | 3.3324 | 3.3324 | 3.3324 | 3.3324 | 3.3324 | 3.3324 | 3.3324 | 3.3324 | 3.3324 | 3.3324 | 3.3324 | 3.3324 | 3.3324 | 3.3324 | 3.3324 | 3.3324 | 3.3324 | 3.3324
CSP tower 9hrs | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | CSP tower 9hrs | 157346 | 157346 | 157346 | 157346 | 157346 | 157346 | 157346 | 157346 | 157346 | 157346 | 157346 | 157346 | 157346 | 157346 | 157346 | 157346 | 157346 | 157346 | 157346 | 157346 | 157346 | 157346 | 157346 | 157346 | 157346 | 157346 | 157346 | 157346
CSP tower 9hrs | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | CSP tower 9hrs | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965
CSP tower 9hrs | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | CSP tower 9hrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CSP tower 9hrs | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | CSP tower 9hrs | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375 | 174064.5375
CSP tower 9hrs | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | CSP tower 9hrs | 60.3% | 60.3% | 60.3% | 60.3% | 60.3% | 60.3% | 60.3% | 60.3% | 60.3% | 60.3% | 60.3% | 60.3% | 60.3% | 60.3% | 60.3% | 60.3% | 60.3% | 60.3% | 60.3% | 60.3% | 60.3% | 60.3% | 60.3% | 60.3% | 60.3% | 60.3% | 60.3% | 60.3%
CSP tower 9hrs | WACC | Apr-23 ZAR | years | IRP 2023 | CSP tower 9hrs | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
CSP tower 9hrs | Lifetime |  | years | EPRI 2021 | CSP tower 9hrs | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
CSP tower 9hrs | Capital recovery factor |  | % | Calculated | CSP tower 9hrs | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051%
CSP tower 9hrs | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | CSP tower 9hrs | 16719.39 | 16719.39 | 16719.39 | 16719.39 | 16719.39 | 16719.39 | 16719.39 | 16719.39 | 16719.39 | 16719.39 | 16719.39 | 16719.39 | 16719.39 | 16719.39 | 16719.39 | 16719.39 | 16719.39 | 16719.39 | 16719.39 | 16719.39 | 16719.39 | 16719.39 | 16719.39 | 16719.39 | 16719.39 | 16719.39 | 16719.39 | 16719.39
CSP tower 9hrs | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | CSP tower 9hrs | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652
CCGT -1 | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | 1X1 9F.05 CCGT | 22001 | 22001 | 22001 | 22001 | 22001 | 22001 | 22001 | 22001 | 22001 | 22001 | 22001 | 22001 | 22001 | 22001 | 22001 | 22001 | 22001 | 22001 | 22001 | 22001 | 22001 | 22001 | 22001 | 22001 | 22001 | 22001 | 22001 | 22001
CCGT -1 | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | 1X1 9F.05 CCGT | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
CCGT -1 | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | 1X1 9F.05 CCGT | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076
CCGT -1 | Heat rate |  | MJ/MWh | EPRI 2021 | 1X1 9F.05 CCGT | 6942 | 6942 | 6942 | 6942 | 6942 | 6942 | 6942 | 6942 | 6942 | 6942 | 6942 | 6942 | 6942 | 6942 | 6942 | 6942 | 6942 | 6942 | 6942 | 6942 | 6942 | 6942 | 6942 | 6942 | 6942 | 6942 | 6942 | 6942
CCGT -1 | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | 1X1 9F.05 CCGT | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95
CCGT -1 | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | 1X1 9F.05 CCGT | 1.8879 | 1.8879 | 1.8879 | 1.8879 | 1.8879 | 1.8879 | 1.8879 | 1.8879 | 1.8879 | 1.8879 | 1.8879 | 1.8879 | 1.8879 | 1.8879 | 1.8879 | 1.8879 | 1.8879 | 1.8879 | 1.8879 | 1.8879 | 1.8879 | 1.8879 | 1.8879 | 1.8879 | 1.8879 | 1.8879 | 1.8879 | 1.8879
CCGT -1 | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | 1X1 9F.05 CCGT | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805 | 24405.4805
CCGT -1 | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | 1X1 9F.05 CCGT | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50%
CCGT -1 | WACC | Apr-23 ZAR | years | IRP 2023 | 1X1 9F.05 CCGT | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
CCGT -1 | Lifetime |  | years | EPRI 2021 | 1X1 9F.05 CCGT | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
CCGT -1 | Capital recovery factor |  | % | Calculated | 1X1 9F.05 CCGT | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051%
CCGT -1 | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | 1X1 9F.05 CCGT | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132 | 2377.9132
CCGT -1 | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | 1X1 9F.05 CCGT | 2.5068 | 2.5068 | 2.5068 | 2.5068 | 2.5068 | 2.5068 | 2.5068 | 2.5068 | 2.5068 | 2.5068 | 2.5068 | 2.5068 | 2.5068 | 2.5068 | 2.5068 | 2.5068 | 2.5068 | 2.5068 | 2.5068 | 2.5068 | 2.5068 | 2.5068 | 2.5068 | 2.5068 | 2.5068 | 2.5068 | 2.5068 | 2.5068
CCGT -2 | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | 2X1 9F.05 CCGT | 16501 | 16501 | 16501 | 16501 | 16501 | 16501 | 16501 | 16501 | 16501 | 16501 | 16501 | 16501 | 16501 | 16501 | 16501 | 16501 | 16501 | 16501 | 16501 | 16501 | 16501 | 16501 | 16501 | 16501 | 16501 | 16501 | 16501 | 16501
CCGT -2 | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | 2X1 9F.05 CCGT | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
CCGT -2 | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | 2X1 9F.05 CCGT | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064
CCGT -2 | Heat rate |  | MJ/MWh | EPRI 2021 | 2X1 9F.05 CCGT | 6900 | 6900 | 6900 | 6900 | 6900 | 6900 | 6900 | 6900 | 6900 | 6900 | 6900 | 6900 | 6900 | 6900 | 6900 | 6900 | 6900 | 6900 | 6900 | 6900 | 6900 | 6900 | 6900 | 6900 | 6900 | 6900 | 6900 | 6900
CCGT -2 | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | 2X1 9F.05 CCGT | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95
CCGT -2 | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | 2X1 9F.05 CCGT | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765
CCGT -2 | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | 2X1 9F.05 CCGT | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877 | 18304.3877
CCGT -2 | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | 2X1 9F.05 CCGT | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50%
CCGT -2 | WACC | Apr-23 ZAR | years | IRP 2023 | 2X1 9F.05 CCGT | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
CCGT -2 | Lifetime |  | years | EPRI 2021 | 2X1 9F.05 CCGT | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
CCGT -2 | Capital recovery factor |  | % | Calculated | 2X1 9F.05 CCGT | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051%
CCGT -2 | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | 2X1 9F.05 CCGT | 1752.71 | 1752.71 | 1752.71 | 1752.71 | 1752.71 | 1752.71 | 1752.71 | 1752.71 | 1752.71 | 1752.71 | 1752.71 | 1752.71 | 1752.71 | 1752.71 | 1752.71 | 1752.71 | 1752.71 | 1752.71 | 1752.71 | 1752.71 | 1752.71 | 1752.71 | 1752.71 | 1752.71 | 1752.71 | 1752.71 | 1752.71 | 1752.71
CCGT -2 | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | 2X1 9F.05 CCGT | 2.3406 | 2.3406 | 2.3406 | 2.3406 | 2.3406 | 2.3406 | 2.3406 | 2.3406 | 2.3406 | 2.3406 | 2.3406 | 2.3406 | 2.3406 | 2.3406 | 2.3406 | 2.3406 | 2.3406 | 2.3406 | 2.3406 | 2.3406 | 2.3406 | 2.3406 | 2.3406 | 2.3406 | 2.3406 | 2.3406 | 2.3406 | 2.3406
CCGT -3 | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | 1X1 9HA.02 CCGT | 16085 | 16085 | 16085 | 16085 | 16085 | 16085 | 16085 | 16085 | 16085 | 16085 | 16085 | 16085 | 16085 | 16085 | 16085 | 16085 | 16085 | 16085 | 16085 | 16085 | 16085 | 16085 | 16085 | 16085 | 16085 | 16085 | 16085 | 16085
CCGT -3 | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | 1X1 9HA.02 CCGT | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99
CCGT -3 | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | 1X1 9HA.02 CCGT | 0.073 | 0.073 | 0.073 | 0.073 | 0.073 | 0.073 | 0.073 | 0.073 | 0.073 | 0.073 | 0.073 | 0.073 | 0.073 | 0.073 | 0.073 | 0.073 | 0.073 | 0.073 | 0.073 | 0.073 | 0.073 | 0.073 | 0.073 | 0.073 | 0.073 | 0.073 | 0.073 | 0.073
CCGT -3 | Heat rate |  | MJ/MWh | EPRI 2021 | 1X1 9HA.02 CCGT | 6499 | 6499 | 6499 | 6499 | 6499 | 6499 | 6499 | 6499 | 6499 | 6499 | 6499 | 6499 | 6499 | 6499 | 6499 | 6499 | 6499 | 6499 | 6499 | 6499 | 6499 | 6499 | 6499 | 6499 | 6499 | 6499 | 6499 | 6499
CCGT -3 | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | 1X1 9HA.02 CCGT | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95
CCGT -3 | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | 1X1 9HA.02 CCGT | 1.7674 | 1.7674 | 1.7674 | 1.7674 | 1.7674 | 1.7674 | 1.7674 | 1.7674 | 1.7674 | 1.7674 | 1.7674 | 1.7674 | 1.7674 | 1.7674 | 1.7674 | 1.7674 | 1.7674 | 1.7674 | 1.7674 | 1.7674 | 1.7674 | 1.7674 | 1.7674 | 1.7674 | 1.7674 | 1.7674 | 1.7674 | 1.7674
CCGT -3 | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | 1X1 9HA.02 CCGT | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232 | 17842.9232
CCGT -3 | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | 1X1 9HA.02 CCGT | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50%
CCGT -3 | WACC | Apr-23 ZAR | years | IRP 2023 | 1X1 9HA.02 CCGT | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
CCGT -3 | Lifetime |  | years | EPRI 2021 | 1X1 9HA.02 CCGT | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
CCGT -3 | Capital recovery factor |  | % | Calculated | 1X1 9HA.02 CCGT | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051%
CCGT -3 | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | 1X1 9HA.02 CCGT | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434 | 1713.9434
CCGT -3 | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | 1X1 9HA.02 CCGT | 2.2317 | 2.2317 | 2.2317 | 2.2317 | 2.2317 | 2.2317 | 2.2317 | 2.2317 | 2.2317 | 2.2317 | 2.2317 | 2.2317 | 2.2317 | 2.2317 | 2.2317 | 2.2317 | 2.2317 | 2.2317 | 2.2317 | 2.2317 | 2.2317 | 2.2317 | 2.2317 | 2.2317 | 2.2317 | 2.2317 | 2.2317 | 2.2317
CCGT -4 | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | 2X1 9HA.02 CCGT | 12664 | 12664 | 12664 | 12664 | 12664 | 12664 | 12664 | 12664 | 12664 | 12664 | 12664 | 12664 | 12664 | 12664 | 12664 | 12664 | 12664 | 12664 | 12664 | 12664 | 12664 | 12664 | 12664 | 12664 | 12664 | 12664 | 12664 | 12664
CCGT -4 | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | 2X1 9HA.02 CCGT | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
CCGT -4 | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | 2X1 9HA.02 CCGT | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
CCGT -4 | Heat rate |  | MJ/MWh | EPRI 2021 | 2X1 9HA.02 CCGT | 6541 | 6541 | 6541 | 6541 | 6541 | 6541 | 6541 | 6541 | 6541 | 6541 | 6541 | 6541 | 6541 | 6541 | 6541 | 6541 | 6541 | 6541 | 6541 | 6541 | 6541 | 6541 | 6541 | 6541 | 6541 | 6541 | 6541 | 6541
CCGT -4 | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | 2X1 9HA.02 CCGT | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95
CCGT -4 | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | 2X1 9HA.02 CCGT | 1.7788 | 1.7788 | 1.7788 | 1.7788 | 1.7788 | 1.7788 | 1.7788 | 1.7788 | 1.7788 | 1.7788 | 1.7788 | 1.7788 | 1.7788 | 1.7788 | 1.7788 | 1.7788 | 1.7788 | 1.7788 | 1.7788 | 1.7788 | 1.7788 | 1.7788 | 1.7788 | 1.7788 | 1.7788 | 1.7788 | 1.7788 | 1.7788
CCGT -4 | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | 2X1 9HA.02 CCGT | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435 | 14048.0435
CCGT -4 | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | 2X1 9HA.02 CCGT | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50%
CCGT -4 | WACC | Apr-23 ZAR | years | IRP 2023 | 2X1 9HA.02 CCGT | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
CCGT -4 | Lifetime |  | years | EPRI 2021 | 2X1 9HA.02 CCGT | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
CCGT -4 | Capital recovery factor |  | % | Calculated | 2X1 9HA.02 CCGT | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051%
CCGT -4 | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | 2X1 9HA.02 CCGT | 1328.473 | 1328.473 | 1328.473 | 1328.473 | 1328.473 | 1328.473 | 1328.473 | 1328.473 | 1328.473 | 1328.473 | 1328.473 | 1328.473 | 1328.473 | 1328.473 | 1328.473 | 1328.473 | 1328.473 | 1328.473 | 1328.473 | 1328.473 | 1328.473 | 1328.473 | 1328.473 | 1328.473 | 1328.473 | 1328.473 | 1328.473 | 1328.473
CCGT -4 | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | 2X1 9HA.02 CCGT | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 2.1421
OCGT-1 | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | 1 x LMS100 SCGT | 23654 | 23654 | 23654 | 23654 | 23654 | 23654 | 23654 | 23654 | 23654 | 23654 | 23654 | 23654 | 23654 | 23654 | 23654 | 23654 | 23654 | 23654 | 23654 | 23654 | 23654 | 23654 | 23654 | 23654 | 23654 | 23654 | 23654 | 23654
OCGT-1 | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | 1 x LMS100 SCGT | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234
OCGT-1 | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | 1 x LMS100 SCGT | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158
OCGT-1 | Heat rate |  | MJ/MWh | EPRI 2021 | 1 x LMS100 SCGT | 9612 | 9612 | 9612 | 9612 | 9612 | 9612 | 9612 | 9612 | 9612 | 9612 | 9612 | 9612 | 9612 | 9612 | 9612 | 9612 | 9612 | 9612 | 9612 | 9612 | 9612 | 9612 | 9612 | 9612 | 9612 | 9612 | 9612 | 9612
OCGT-1 | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | 1 x LMS100 SCGT | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95
OCGT-1 | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | 1 x LMS100 SCGT | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614
OCGT-1 | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | 1 x LMS100 SCGT | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652 | 25399.6652
OCGT-1 | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | 1 x LMS100 SCGT | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10%
OCGT-1 | WACC | Apr-23 ZAR | years | IRP 2023 | 1 x LMS100 SCGT | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
OCGT-1 | Lifetime |  | years | EPRI 2021 | 1 x LMS100 SCGT | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
OCGT-1 | Capital recovery factor |  | % | Calculated | 1 x LMS100 SCGT | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051%
OCGT-1 | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | 1 x LMS100 SCGT | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958 | 2532.8958
OCGT-1 | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | 1 x LMS100 SCGT | 5.6634 | 5.6634 | 5.6634 | 5.6634 | 5.6634 | 5.6634 | 5.6634 | 5.6634 | 5.6634 | 5.6634 | 5.6634 | 5.6634 | 5.6634 | 5.6634 | 5.6634 | 5.6634 | 5.6634 | 5.6634 | 5.6634 | 5.6634 | 5.6634 | 5.6634 | 5.6634 | 5.6634 | 5.6634 | 5.6634 | 5.6634 | 5.6634
OCGT-2 | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | 1x 9F.05 SCGT | 13217 | 13217 | 13217 | 13217 | 13217 | 13217 | 13217 | 13217 | 13217 | 13217 | 13217 | 13217 | 13217 | 13217 | 13217 | 13217 | 13217 | 13217 | 13217 | 13217 | 13217 | 13217 | 13217 | 13217 | 13217 | 13217 | 13217 | 13217
OCGT-2 | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | 1x 9F.05 SCGT | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107
OCGT-2 | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | 1x 9F.05 SCGT | 0.081 | 0.081 | 0.081 | 0.081 | 0.081 | 0.081 | 0.081 | 0.081 | 0.081 | 0.081 | 0.081 | 0.081 | 0.081 | 0.081 | 0.081 | 0.081 | 0.081 | 0.081 | 0.081 | 0.081 | 0.081 | 0.081 | 0.081 | 0.081 | 0.081 | 0.081 | 0.081 | 0.081
OCGT-2 | Heat rate |  | MJ/MWh | EPRI 2021 | 1x 9F.05 SCGT | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453
OCGT-2 | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | 1x 9F.05 SCGT | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95
OCGT-2 | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | 1x 9F.05 SCGT | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707
OCGT-2 | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | 1x 9F.05 SCGT | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146 | 14192.4146
OCGT-2 | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | 1x 9F.05 SCGT | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10%
OCGT-2 | WACC | Apr-23 ZAR | years | IRP 2023 | 1x 9F.05 SCGT | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
OCGT-2 | Lifetime |  | years | EPRI 2021 | 1x 9F.05 SCGT | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
OCGT-2 | Capital recovery factor |  | % | Calculated | 1x 9F.05 SCGT | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051%
OCGT-2 | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | 1x 9F.05 SCGT | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398 | 1391.5398
OCGT-2 | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | 1x 9F.05 SCGT | 4.2403 | 4.2403 | 4.2403 | 4.2403 | 4.2403 | 4.2403 | 4.2403 | 4.2403 | 4.2403 | 4.2403 | 4.2403 | 4.2403 | 4.2403 | 4.2403 | 4.2403 | 4.2403 | 4.2403 | 4.2403 | 4.2403 | 4.2403 | 4.2403 | 4.2403 | 4.2403 | 4.2403 | 4.2403 | 4.2403 | 4.2403 | 4.2403
OCGT-3 | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | 1x 9HA.02 SCGT | 11345 | 11345 | 11345 | 11345 | 11345 | 11345 | 11345 | 11345 | 11345 | 11345 | 11345 | 11345 | 11345 | 11345 | 11345 | 11345 | 11345 | 11345 | 11345 | 11345 | 11345 | 11345 | 11345 | 11345 | 11345 | 11345 | 11345 | 11345
OCGT-3 | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | 1x 9HA.02 SCGT | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
OCGT-3 | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | 1x 9HA.02 SCGT | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078
OCGT-3 | Heat rate |  | MJ/MWh | EPRI 2021 | 1x 9HA.02 SCGT | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453 | 9453
OCGT-3 | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | 1x 9HA.02 SCGT | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95
OCGT-3 | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | 1x 9HA.02 SCGT | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707 | 2.5707
OCGT-3 | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | 1x 9HA.02 SCGT | 12182.261 | 12182.261 | 12182.261 | 12182.261 | 12182.261 | 12182.261 | 12182.261 | 12182.261 | 12182.261 | 12182.261 | 12182.261 | 12182.261 | 12182.261 | 12182.261 | 12182.261 | 12182.261 | 12182.261 | 12182.261 | 12182.261 | 12182.261 | 12182.261 | 12182.261 | 12182.261 | 12182.261 | 12182.261 | 12182.261 | 12182.261 | 12182.261
OCGT-3 | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | 1x 9HA.02 SCGT | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10%
OCGT-3 | WACC | Apr-23 ZAR | years | IRP 2023 | 1x 9HA.02 SCGT | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
OCGT-3 | Lifetime |  | years | EPRI 2021 | 1x 9HA.02 SCGT | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
OCGT-3 | Capital recovery factor |  | % | Calculated | 1x 9HA.02 SCGT | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051%
OCGT-3 | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | 1x 9HA.02 SCGT | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031 | 1163.6031
OCGT-3 | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | 1x 9HA.02 SCGT | 3.9771 | 3.9771 | 3.9771 | 3.9771 | 3.9771 | 3.9771 | 3.9771 | 3.9771 | 3.9771 | 3.9771 | 3.9771 | 3.9771 | 3.9771 | 3.9771 | 3.9771 | 3.9771 | 3.9771 | 3.9771 | 3.9771 | 3.9771 | 3.9771 | 3.9771 | 3.9771 | 3.9771 | 3.9771 | 3.9771 | 3.9771 | 3.9771
ICE-1 | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | 1x9 MW ICE | 62146 | 62146 | 62146 | 62146 | 62146 | 62146 | 62146 | 62146 | 62146 | 62146 | 62146 | 62146 | 62146 | 62146 | 62146 | 62146 | 62146 | 62146 | 62146 | 62146 | 62146 | 62146 | 62146 | 62146 | 62146 | 62146 | 62146 | 62146
ICE-1 | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | 1x9 MW ICE | 1316 | 1316 | 1316 | 1316 | 1316 | 1316 | 1316 | 1316 | 1316 | 1316 | 1316 | 1316 | 1316 | 1316 | 1316 | 1316 | 1316 | 1316 | 1316 | 1316 | 1316 | 1316 | 1316 | 1316 | 1316 | 1316 | 1316 | 1316
ICE-1 | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | 1x9 MW ICE | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134
ICE-1 | Heat rate |  | MJ/MWh | EPRI 2021 | 1x9 MW ICE | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042
ICE-1 | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | 1x9 MW ICE | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95
ICE-1 | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | 1x9 MW ICE | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459
ICE-1 | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | 1x9 MW ICE | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748 | 66732.3748
ICE-1 | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | 1x9 MW ICE | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10%
ICE-1 | WACC | Apr-23 ZAR | years | IRP 2023 | 1x9 MW ICE | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
ICE-1 | Lifetime |  | years | EPRI 2021 | 1x9 MW ICE | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
ICE-1 | Capital recovery factor |  | % | Calculated | 1x9 MW ICE | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051%
ICE-1 | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | 1x9 MW ICE | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739 | 7355.8739
ICE-1 | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | 1x9 MW ICE | 10.9901 | 10.9901 | 10.9901 | 10.9901 | 10.9901 | 10.9901 | 10.9901 | 10.9901 | 10.9901 | 10.9901 | 10.9901 | 10.9901 | 10.9901 | 10.9901 | 10.9901 | 10.9901 | 10.9901 | 10.9901 | 10.9901 | 10.9901 | 10.9901 | 10.9901 | 10.9901 | 10.9901 | 10.9901 | 10.9901 | 10.9901 | 10.9901
ICE-2 | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | 1x18 MW ICE | 50925 | 50925 | 50925 | 50925 | 50925 | 50925 | 50925 | 50925 | 50925 | 50925 | 50925 | 50925 | 50925 | 50925 | 50925 | 50925 | 50925 | 50925 | 50925 | 50925 | 50925 | 50925 | 50925 | 50925 | 50925 | 50925 | 50925 | 50925
ICE-2 | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | 1x18 MW ICE | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920
ICE-2 | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | 1x18 MW ICE | 0.142 | 0.142 | 0.142 | 0.142 | 0.142 | 0.142 | 0.142 | 0.142 | 0.142 | 0.142 | 0.142 | 0.142 | 0.142 | 0.142 | 0.142 | 0.142 | 0.142 | 0.142 | 0.142 | 0.142 | 0.142 | 0.142 | 0.142 | 0.142 | 0.142 | 0.142 | 0.142 | 0.142
ICE-2 | Heat rate |  | MJ/MWh | EPRI 2021 | 1x18 MW ICE | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042 | 9042
ICE-2 | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | 1x18 MW ICE | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95
ICE-2 | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | 1x18 MW ICE | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459 | 2.459
ICE-2 | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | 1x18 MW ICE | 54683.265 | 54683.265 | 54683.265 | 54683.265 | 54683.265 | 54683.265 | 54683.265 | 54683.265 | 54683.265 | 54683.265 | 54683.265 | 54683.265 | 54683.265 | 54683.265 | 54683.265 | 54683.265 | 54683.265 | 54683.265 | 54683.265 | 54683.265 | 54683.265 | 54683.265 | 54683.265 | 54683.265 | 54683.265 | 54683.265 | 54683.265 | 54683.265
ICE-2 | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | 1x18 MW ICE | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10%
ICE-2 | WACC | Apr-23 ZAR | years | IRP 2023 | 1x18 MW ICE | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
ICE-2 | Lifetime |  | years | EPRI 2021 | 1x18 MW ICE | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
ICE-2 | Capital recovery factor |  | % | Calculated | 1x18 MW ICE | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051%
ICE-2 | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | 1x18 MW ICE | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222 | 5869.3222
ICE-2 | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | 1x18 MW ICE | 9.3011 | 9.3011 | 9.3011 | 9.3011 | 9.3011 | 9.3011 | 9.3011 | 9.3011 | 9.3011 | 9.3011 | 9.3011 | 9.3011 | 9.3011 | 9.3011 | 9.3011 | 9.3011 | 9.3011 | 9.3011 | 9.3011 | 9.3011 | 9.3011 | 9.3011 | 9.3011 | 9.3011 | 9.3011 | 9.3011 | 9.3011 | 9.3011
CCGT-ICE | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | 18 MW ICE, 12x1 Combined | 32892 | 32892 | 32892 | 32892 | 32892 | 32892 | 32892 | 32892 | 32892 | 32892 | 32892 | 32892 | 32892 | 32892 | 32892 | 32892 | 32892 | 32892 | 32892 | 32892 | 32892 | 32892 | 32892 | 32892 | 32892 | 32892 | 32892 | 32892
CCGT-ICE | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | 18 MW ICE, 12x1 Combined | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287
CCGT-ICE | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | 18 MW ICE, 12x1 Combined | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076
CCGT-ICE | Heat rate |  | MJ/MWh | EPRI 2021 | 18 MW ICE, 12x1 Combined | 8419 | 8419 | 8419 | 8419 | 8419 | 8419 | 8419 | 8419 | 8419 | 8419 | 8419 | 8419 | 8419 | 8419 | 8419 | 8419 | 8419 | 8419 | 8419 | 8419 | 8419 | 8419 | 8419 | 8419 | 8419 | 8419 | 8419 | 8419
CCGT-ICE | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | 18 MW ICE, 12x1 Combined | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95 | 271.95
CCGT-ICE | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | 18 MW ICE, 12x1 Combined | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895
CCGT-ICE | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | 18 MW ICE, 12x1 Combined | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296 | 35319.4296
CCGT-ICE | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | 18 MW ICE, 12x1 Combined | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50%
CCGT-ICE | WACC | Apr-23 ZAR | years | IRP 2023 | 18 MW ICE, 12x1 Combined | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
CCGT-ICE | Lifetime |  | years | EPRI 2021 | 18 MW ICE, 12x1 Combined | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
CCGT-ICE | Capital recovery factor |  | % | Calculated | 18 MW ICE, 12x1 Combined | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051%
CCGT-ICE | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | 18 MW ICE, 12x1 Combined | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228 | 3483.7228
CCGT-ICE | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | 18 MW ICE, 12x1 Combined | 3.1609 | 3.1609 | 3.1609 | 3.1609 | 3.1609 | 3.1609 | 3.1609 | 3.1609 | 3.1609 | 3.1609 | 3.1609 | 3.1609 | 3.1609 | 3.1609 | 3.1609 | 3.1609 | 3.1609 | 3.1609 | 3.1609 | 3.1609 | 3.1609 | 3.1609 | 3.1609 | 3.1609 | 3.1609 | 3.1609 | 3.1609 | 3.1609
Coal - no CCS -1 | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | Coal PF wt FGD | 62168 | 62168 | 62168 | 62168 | 62168 | 62168 | 62168 | 62168 | 62168 | 62168 | 62168 | 62168 | 62168 | 62168 | 62168 | 62168 | 62168 | 62168 | 62168 | 62168 | 62168 | 62168 | 62168 | 62168 | 62168 | 62168 | 62168 | 62168
Coal - no CCS -1 | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | Coal PF wt FGD | 1439 | 1439 | 1439 | 1439 | 1439 | 1439 | 1439 | 1439 | 1439 | 1439 | 1439 | 1439 | 1439 | 1439 | 1439 | 1439 | 1439 | 1439 | 1439 | 1439 | 1439 | 1439 | 1439 | 1439 | 1439 | 1439 | 1439 | 1439
Coal - no CCS -1 | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | Coal PF wt FGD | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
Coal - no CCS -1 | Heat rate |  | MJ/MWh | EPRI 2021 | Coal PF wt FGD | 9776 | 9776 | 9776 | 9776 | 9776 | 9776 | 9776 | 9776 | 9776 | 9776 | 9776 | 9776 | 9776 | 9776 | 9776 | 9776 | 9776 | 9776 | 9776 | 9776 | 9776 | 9776 | 9776 | 9776 | 9776 | 9776 | 9776 | 9776
Coal - no CCS -1 | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | Coal PF wt FGD | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18
Coal - no CCS -1 | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | Coal PF wt FGD | 0.44168 | 0.44168 | 0.44168 | 0.44168 | 0.44168 | 0.44168 | 0.44168 | 0.44168 | 0.44168 | 0.44168 | 0.44168 | 0.44168 | 0.44168 | 0.44168 | 0.44168 | 0.44168 | 0.44168 | 0.44168 | 0.44168 | 0.44168 | 0.44168 | 0.44168 | 0.44168 | 0.44168 | 0.44168 | 0.44168 | 0.44168 | 0.44168
Coal - no CCS -1 | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | Coal PF wt FGD | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259 | 68942.7259
Coal - no CCS -1 | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | Coal PF wt FGD | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
Coal - no CCS -1 | WACC | Apr-23 ZAR | years | IRP 2023 | Coal PF wt FGD | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
Coal - no CCS -1 | Lifetime |  | years | EPRI 2021 | Coal PF wt FGD | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Coal - no CCS -1 | Capital recovery factor |  | % | Calculated | Coal PF wt FGD | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051%
Coal - no CCS -1 | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | Coal PF wt FGD | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303 | 7678.9303
Coal - no CCS -1 | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | Coal PF wt FGD | 1.513 | 1.513 | 1.513 | 1.513 | 1.513 | 1.513 | 1.513 | 1.513 | 1.513 | 1.513 | 1.513 | 1.513 | 1.513 | 1.513 | 1.513 | 1.513 | 1.513 | 1.513 | 1.513 | 1.513 | 1.513 | 1.513 | 1.513 | 1.513 | 1.513 | 1.513 | 1.513 | 1.513
Coal - no CCS -2 | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | Coal FBC wt FGD, single unit | 73639 | 73639 | 73639 | 73639 | 73639 | 73639 | 73639 | 73639 | 73639 | 73639 | 73639 | 73639 | 73639 | 73639 | 73639 | 73639 | 73639 | 73639 | 73639 | 73639 | 73639 | 73639 | 73639 | 73639 | 73639 | 73639 | 73639 | 73639
Coal - no CCS -2 | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | Coal FBC wt FGD, single unit | 984 | 984 | 984 | 984 | 984 | 984 | 984 | 984 | 984 | 984 | 984 | 984 | 984 | 984 | 984 | 984 | 984 | 984 | 984 | 984 | 984 | 984 | 984 | 984 | 984 | 984 | 984 | 984
Coal - no CCS -2 | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | Coal FBC wt FGD, single unit | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188
Coal - no CCS -2 | Heat rate |  | MJ/MWh | EPRI 2021 | Coal FBC wt FGD, single unit | 13990 | 13990 | 13990 | 13990 | 13990 | 13990 | 13990 | 13990 | 13990 | 13990 | 13990 | 13990 | 13990 | 13990 | 13990 | 13990 | 13990 | 13990 | 13990 | 13990 | 13990 | 13990 | 13990 | 13990 | 13990 | 13990 | 13990 | 13990
Coal - no CCS -2 | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | Coal FBC wt FGD, single unit | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18 | 45.18
Coal - no CCS -2 | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | Coal FBC wt FGD, single unit | 0.63207 | 0.63207 | 0.63207 | 0.63207 | 0.63207 | 0.63207 | 0.63207 | 0.63207 | 0.63207 | 0.63207 | 0.63207 | 0.63207 | 0.63207 | 0.63207 | 0.63207 | 0.63207 | 0.63207 | 0.63207 | 0.63207 | 0.63207 | 0.63207 | 0.63207 | 0.63207 | 0.63207 | 0.63207 | 0.63207 | 0.63207 | 0.63207
Coal - no CCS -2 | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | Coal FBC wt FGD, single unit | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722 | 81663.7722
Coal - no CCS -2 | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | Coal FBC wt FGD, single unit | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
Coal - no CCS -2 | WACC | Apr-23 ZAR | years | IRP 2023 | Coal FBC wt FGD, single unit | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
Coal - no CCS -2 | Lifetime |  | years | EPRI 2021 | Coal FBC wt FGD, single unit | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Coal - no CCS -2 | Capital recovery factor |  | % | Calculated | Coal FBC wt FGD, single unit | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051% | 9.051%
Coal - no CCS -2 | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | Coal FBC wt FGD, single unit | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983 | 8375.2983
Coal - no CCS -2 | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | Coal FBC wt FGD, single unit | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449
Nuclear - SMR -1 | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | Nuclear SMR | 140302 | 140302 | 140302 | 140302 | 140302 | 140302 | 140302 | 140302 | 140302 | 140302 | 140302 | 140302 | 140302 | 140302 | 140302 | 140302 | 140302 | 140302 | 140302 | 140302 | 140302 | 140302 | 140302 | 140302 | 140302 | 140302 | 140302 | 140302
Nuclear - SMR -1 | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | Nuclear SMR | 2230 | 2230 | 2230 | 2230 | 2230 | 2230 | 2230 | 2230 | 2230 | 2230 | 2230 | 2230 | 2230 | 2230 | 2230 | 2230 | 2230 | 2230 | 2230 | 2230 | 2230 | 2230 | 2230 | 2230 | 2230 | 2230 | 2230 | 2230
Nuclear - SMR -1 | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | Nuclear SMR | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013
Nuclear - SMR -1 | Heat rate |  | MJ/MWh | EPRI 2021 | Nuclear SMR | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996
Nuclear - SMR -1 | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | Nuclear SMR | 14.22 | 14.22 | 14.22 | 14.22 | 14.22 | 14.22 | 14.22 | 14.22 | 14.22 | 14.22 | 14.22 | 14.22 | 14.22 | 14.22 | 14.22 | 14.22 | 14.22 | 14.22 | 14.22 | 14.22 | 14.22 | 14.22 | 14.22 | 14.22 | 14.22 | 14.22 | 14.22 | 14.22
Nuclear - SMR -1 | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | Nuclear SMR | 0.17058 | 0.17058 | 0.17058 | 0.17058 | 0.17058 | 0.17058 | 0.17058 | 0.17058 | 0.17058 | 0.17058 | 0.17058 | 0.17058 | 0.17058 | 0.17058 | 0.17058 | 0.17058 | 0.17058 | 0.17058 | 0.17058 | 0.17058 | 0.17058 | 0.17058 | 0.17058 | 0.17058 | 0.17058 | 0.17058 | 0.17058 | 0.17058
Nuclear - SMR -1 | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | Nuclear SMR | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694 | 174759.9694
Nuclear - SMR -1 | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | Nuclear SMR | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90%
Nuclear - SMR -1 | WACC | Apr-23 ZAR | years | IRP 2023 | Nuclear SMR | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
Nuclear - SMR -1 | Lifetime |  | years | EPRI 2021 | Nuclear SMR | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Nuclear - SMR -1 | Capital recovery factor |  | % | Calculated | Nuclear SMR | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273%
Nuclear - SMR -1 | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | Nuclear SMR | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012 | 16688.1012
Nuclear - SMR -1 | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | Nuclear SMR | 2.3003 | 2.3003 | 2.3003 | 2.3003 | 2.3003 | 2.3003 | 2.3003 | 2.3003 | 2.3003 | 2.3003 | 2.3003 | 2.3003 | 2.3003 | 2.3003 | 2.3003 | 2.3003 | 2.3003 | 2.3003 | 2.3003 | 2.3003 | 2.3003 | 2.3003 | 2.3003 | 2.3003 | 2.3003 | 2.3003 | 2.3003 | 2.3003
Nuclear - SMR -2 | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | SMR-NS 1 | 107910 | 107910 | 107910 | 107910 | 107910 | 107910 | 107910 | 107910 | 107910 | 107910 | 107910 | 107910 | 107910 | 107910 | 107910 | 107910 | 107910 | 107910 | 107910 | 107910 | 107910 | 107910 | 107910 | 107910 | 107910 | 107910 | 107910 | 107910
Nuclear - SMR -2 | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | SMR-NS 1 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646
Nuclear - SMR -2 | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | SMR-NS 1 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045
Nuclear - SMR -2 | Heat rate |  | MJ/MWh | EPRI 2021 | SMR-NS 1 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996
Nuclear - SMR -2 | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | SMR-NS 1 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93
Nuclear - SMR -2 | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | SMR-NS 1 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509
Nuclear - SMR -2 | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | SMR-NS 1 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408 | 134412.5408
Nuclear - SMR -2 | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | SMR-NS 1 | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90%
Nuclear - SMR -2 | WACC | Apr-23 ZAR | years | IRP 2023 | SMR-NS 1 | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
Nuclear - SMR -2 | Lifetime |  | years | EPRI 2021 | SMR-NS 1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Nuclear - SMR -2 | Capital recovery factor |  | % | Calculated | SMR-NS 1 | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273%
Nuclear - SMR -2 | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | SMR-NS 1 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102 | 12766.1102
Nuclear - SMR -2 | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | SMR-NS 1 | 1.8793 | 1.8793 | 1.8793 | 1.8793 | 1.8793 | 1.8793 | 1.8793 | 1.8793 | 1.8793 | 1.8793 | 1.8793 | 1.8793 | 1.8793 | 1.8793 | 1.8793 | 1.8793 | 1.8793 | 1.8793 | 1.8793 | 1.8793 | 1.8793 | 1.8793 | 1.8793 | 1.8793 | 1.8793 | 1.8793 | 1.8793 | 1.8793
Nuclear - SMR -3 | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | SMR-UK 2 | 120498 | 120498 | 120498 | 120498 | 120498 | 120498 | 120498 | 120498 | 120498 | 120498 | 120498 | 120498 | 120498 | 120498 | 120498 | 120498 | 120498 | 120498 | 120498 | 120498 | 120498 | 120498 | 120498 | 120498 | 120498 | 120498 | 120498 | 120498
Nuclear - SMR -3 | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | SMR-UK 2 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646
Nuclear - SMR -3 | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | SMR-UK 2 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045
Nuclear - SMR -3 | Heat rate |  | MJ/MWh | EPRI 2021 | SMR-UK 2 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996
Nuclear - SMR -3 | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | SMR-UK 2 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93
Nuclear - SMR -3 | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | SMR-UK 2 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509
Nuclear - SMR -3 | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | SMR-UK 2 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355 | 150092.1355
Nuclear - SMR -3 | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | SMR-UK 2 | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90%
Nuclear - SMR -3 | WACC | Apr-23 ZAR | years | IRP 2023 | SMR-UK 2 | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
Nuclear - SMR -3 | Lifetime |  | years | EPRI 2021 | SMR-UK 2 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Nuclear - SMR -3 | Capital recovery factor |  | % | Calculated | SMR-UK 2 | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273%
Nuclear - SMR -3 | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | SMR-UK 2 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018 | 14063.3018
Nuclear - SMR -3 | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | SMR-UK 2 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439
Nuclear - SMR -4 | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | SMR-CP 3 | 141397 | 141397 | 141397 | 141397 | 141397 | 141397 | 141397 | 141397 | 141397 | 141397 | 141397 | 141397 | 141397 | 141397 | 141397 | 141397 | 141397 | 141397 | 141397 | 141397 | 141397 | 141397 | 141397 | 141397 | 141397 | 141397 | 141397 | 141397
Nuclear - SMR -4 | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | SMR-CP 3 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646
Nuclear - SMR -4 | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | SMR-CP 3 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045
Nuclear - SMR -4 | Heat rate |  | MJ/MWh | EPRI 2021 | SMR-CP 3 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996
Nuclear - SMR -4 | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | SMR-CP 3 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93
Nuclear - SMR -4 | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | SMR-CP 3 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509
Nuclear - SMR -4 | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | SMR-CP 3 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986 | 151832.0986
Nuclear - SMR -4 | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | SMR-CP 3 | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90%
Nuclear - SMR -4 | WACC | Apr-23 ZAR | years | IRP 2023 | SMR-CP 3 | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
Nuclear - SMR -4 | Lifetime |  | years | EPRI 2021 | SMR-CP 3 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Nuclear - SMR -4 | Capital recovery factor |  | % | Calculated | SMR-CP 3 | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273%
Nuclear - SMR -4 | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | SMR-CP 3 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511 | 14207.2511
Nuclear - SMR -4 | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | SMR-CP 3 | 2.0621 | 2.0621 | 2.0621 | 2.0621 | 2.0621 | 2.0621 | 2.0621 | 2.0621 | 2.0621 | 2.0621 | 2.0621 | 2.0621 | 2.0621 | 2.0621 | 2.0621 | 2.0621 | 2.0621 | 2.0621 | 2.0621 | 2.0621 | 2.0621 | 2.0621 | 2.0621 | 2.0621 | 2.0621 | 2.0621 | 2.0621 | 2.0621
Nuclear - SMR -5 | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | SMR-GC 1 | 157775 | 157775 | 157775 | 157775 | 157775 | 157775 | 157775 | 157775 | 157775 | 157775 | 157775 | 157775 | 157775 | 157775 | 157775 | 157775 | 157775 | 157775 | 157775 | 157775 | 157775 | 157775 | 157775 | 157775 | 157775 | 157775 | 157775 | 157775
Nuclear - SMR -5 | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | SMR-GC 1 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646
Nuclear - SMR -5 | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | SMR-GC 1 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045
Nuclear - SMR -5 | Heat rate |  | MJ/MWh | EPRI 2021 | SMR-GC 1 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996 | 11996
Nuclear - SMR -5 | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | SMR-GC 1 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93
Nuclear - SMR -5 | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | SMR-GC 1 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509 | 0.21509
Nuclear - SMR -5 | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | SMR-GC 1 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131 | 196524.3131
Nuclear - SMR -5 | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | SMR-GC 1 | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90%
Nuclear - SMR -5 | WACC | Apr-23 ZAR | years | IRP 2023 | SMR-GC 1 | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
Nuclear - SMR -5 | Lifetime |  | years | EPRI 2021 | SMR-GC 1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Nuclear - SMR -5 | Capital recovery factor |  | % | Calculated | SMR-GC 1 | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273%
Nuclear - SMR -5 | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | SMR-GC 1 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914 | 17904.6914
Nuclear - SMR -5 | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | SMR-GC 1 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 2.5311
Nuclear - PWR -1 | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | PWR-CP | 67288 | 67288 | 67288 | 67288 | 67288 | 67288 | 67288 | 67288 | 67288 | 67288 | 67288 | 67288 | 67288 | 67288 | 67288 | 67288 | 67288 | 67288 | 67288 | 67288 | 67288 | 67288 | 67288 | 67288 | 67288 | 67288 | 67288 | 67288
Nuclear - PWR -1 | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | PWR-CP | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646
Nuclear - PWR -1 | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | PWR-CP | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045
Nuclear - PWR -1 | Heat rate |  | MJ/MWh | EPRI 2021 | PWR-CP | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250
Nuclear - PWR -1 | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | PWR-CP | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93
Nuclear - PWR -1 | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | PWR-CP | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171
Nuclear - PWR -1 | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | PWR-CP | 83813.836 | 83813.836 | 83813.836 | 83813.836 | 83813.836 | 83813.836 | 83813.836 | 83813.836 | 83813.836 | 83813.836 | 83813.836 | 83813.836 | 83813.836 | 83813.836 | 83813.836 | 83813.836 | 83813.836 | 83813.836 | 83813.836 | 83813.836 | 83813.836 | 83813.836 | 83813.836 | 83813.836 | 83813.836 | 83813.836 | 83813.836 | 83813.836
Nuclear - PWR -1 | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | PWR-CP | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90%
Nuclear - PWR -1 | WACC | Apr-23 ZAR | years | IRP 2023 | PWR-CP | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
Nuclear - PWR -1 | Lifetime |  | years | EPRI 2021 | PWR-CP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Nuclear - PWR -1 | Capital recovery factor |  | % | Calculated | PWR-CP | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273%
Nuclear - PWR -1 | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | PWR-CP | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189 | 8580.0189
Nuclear - PWR -1 | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | PWR-CP | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335
Nuclear - PWR -2 | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | PWR-AP | 78700 | 78700 | 78700 | 78700 | 78700 | 78700 | 78700 | 78700 | 78700 | 78700 | 78700 | 78700 | 78700 | 78700 | 78700 | 78700 | 78700 | 78700 | 78700 | 78700 | 78700 | 78700 | 78700 | 78700 | 78700 | 78700 | 78700 | 78700
Nuclear - PWR -2 | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | PWR-AP | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646 | 1646
Nuclear - PWR -2 | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | PWR-AP | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045
Nuclear - PWR -2 | Heat rate |  | MJ/MWh | EPRI 2021 | PWR-AP | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250 | 11250
Nuclear - PWR -2 | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | PWR-AP | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93 | 17.93
Nuclear - PWR -2 | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | PWR-AP | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171 | 0.20171
Nuclear - PWR -2 | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | PWR-AP | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068 | 98028.6068
Nuclear - PWR -2 | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | PWR-AP | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90%
Nuclear - PWR -2 | WACC | Apr-23 ZAR | years | IRP 2023 | PWR-AP | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
Nuclear - PWR -2 | Lifetime |  | years | EPRI 2021 | PWR-AP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Nuclear - PWR -2 | Capital recovery factor |  | % | Calculated | PWR-AP | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273% | 8.273%
Nuclear - PWR -2 | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | PWR-AP | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239 | 9756.0239
Nuclear - PWR -2 | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | PWR-AP | 1.4842 | 1.4842 | 1.4842 | 1.4842 | 1.4842 | 1.4842 | 1.4842 | 1.4842 | 1.4842 | 1.4842 | 1.4842 | 1.4842 | 1.4842 | 1.4842 | 1.4842 | 1.4842 | 1.4842 | 1.4842 | 1.4842 | 1.4842 | 1.4842 | 1.4842 | 1.4842 | 1.4842 | 1.4842 | 1.4842 | 1.4842 | 1.4842

## PCC 2022
Technology | Parameter | Currency reference | Units | Source | Description | 2020 | 2025 | 2030 | 2035 | 2050
Wind | Overnight capital cost | 2015 ZAR | ZAR/kW | PCC 2022 | Wind | 12500 | 12391 | 12283 | 12069 | 11859
Wind | Overnight capital cost | Apr-23 ZAR | ZAR/kW | Calculated | Wind | 18454.7908 | 18293.865 | 18134.4157 | 17818.4696 | 17508.4291 | 1.4764
Wind | FOM | 2015 ZAR | ZAR/kW/yr | PCC 2022 | Wind | 611 | 611 | 611 | 611 | 611
Wind | FOM | Apr-23 ZAR | ZAR/kW/yr | Calculated | Wind | 902.0702 | 902.0702 | 902.0702 | 902.0702 | 902.0702
Wind | VOM | 2015 ZAR | ZAR/kWh | PCC 2022 | Wind | 0 | 0 | 0 | 0 | 0
Wind | VOM | Apr-23 ZAR | ZAR/kWh | Calculated | Wind | 0 | 0 | 0 | 0 | 0
Wind | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | Wind | 19009.7701 | 18844.0049 | 18679.7605 | 18354.3132 | 18034.9491
Wind | Capacity factor | Apr-23 ZAR | % | ERPI 2021 | Wind | 36.3% | 36.3% | 36.3% | 36.3% | 36.3%
Wind | WACC | Apr-23 ZAR | % | IRP 2023 | Wind | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
Wind | Lifetime |  | years | PCC 2022 | Wind | 25 | 25 | 25 | 25 | 25
Wind | Capital recovery factor |  | % | Calculated | Wind | 9.528% | 9.528% | 9.528% | 9.528% | 9.528%
Wind | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | Wind | 2713.4036 | 2697.6088 | 2681.9588 | 2650.9488 | 2620.5184
Wind | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | Wind | 0.8533 | 0.84834 | 0.84342 | 0.83366 | 0.82409
Technology | Parameter | Currency reference | Units | Source | Description | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
Wind | Overnight capital cost | Apr-23 ZAR | ZAR/kW | IRP 2023 | Wind | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657 | 31374.6657
Wind | FOM | Apr-23 ZAR | ZAR/kW/yr | IRP 2023 | Wind | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955 | 955
Wind | VOM | Apr-23 ZAR | ZAR/kWh | IRP 2023 | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | Wind | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762 | 32318.1762
Wind | Capacity factor | Apr-23 ZAR | % | EPRI 2021 | Wind | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3% | 36.3%
Wind | WACC | Apr-23 ZAR | % | IRP 2023 | Wind | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2%
Wind | Lifetime |  | years | EPRI 2021 | Wind | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Wind | Capital recovery factor |  | % | Calculated | Wind | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528% | 9.528%
Wind | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | Wind | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161 | 4034.4161
Wind | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | Wind | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687 | 1.2687
Solar PV tracking | Overnight capital cost | 2015 ZAR | ZAR/kW | PCC 2022 | Solar PV tracking | 0.8533 2023: 10471; 0.84834 2024: 9829; 0.84342 2025: 9234; 0.83366 2026: 8203; 0.82409 2027: 7247
Solar PV tracking | Overnight capital cost | Apr-23 ZAR | ZAR/kW | Calculated | Solar PV tracking | 0.8533 2023: 15459.2092; 0.84834 2024: 14511.3711; 0.84342 2025: 13632.9231; 0.83366 2026: 12110.7719; 0.82409 2027: 10699.3495
Solar PV tracking | FOM | 2015 ZAR | ZAR/kW/yr | PCC 2022 | Solar PV tracking | 0.8533 2023: 286; 0.84834 2024: 286; 0.84342 2025: 286; 0.83366 2026: 286; 0.82409 2027: 286
Solar PV tracking | FOM | Apr-23 ZAR | ZAR/kW/yr | Calculated | Solar PV tracking | 0.8533 2023: 422.2456; 0.84834 2024: 422.2456; 0.84342 2025: 422.2456; 0.83366 2026: 422.2456; 0.82409 2027: 422.2456
Solar PV tracking | VOM | 2015 ZAR | ZAR/kWh | PCC 2022 | Solar PV tracking | 0.8533 2023: 0; 0.84834 2024: 0; 0.84342 2025: 0; 0.83366 2026: 0; 0.82409 2027: 0
Solar PV tracking | VOM | Apr-23 ZAR | ZAR/kWh | Calculated | Solar PV tracking | 0.8533 2023: 0; 0.84834 2024: 0; 0.84342 2025: 0; 0.83366 2026: 0; 0.82409 2027: 0
Solar PV tracking | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | Solar PV tracking | 0.8533 2023: 15922.9855; 0.84834 2024: 14946.7123; 0.84342 2025: 14041.9108; 0.83366 2026: 12474.0951; 0.82409 2027: 11020.33
Solar PV tracking | Capacity factor | Apr-23 ZAR | % | ERPI 2021 | Solar PV tracking | 0.8533 2023: 25%; 0.84834 2024: 25%; 0.84342 2025: 25%; 0.83366 2026: 25%; 0.82409 2027: 25%
Solar PV tracking | WACC | Apr-23 ZAR | % | IRP 2023 | Solar PV tracking | 0.8533 2023: 8.2%; 0.84834 2024: 8.2%; 0.84342 2025: 8.2%; 0.83366 2026: 8.2%; 0.82409 2027: 8.2%
Solar PV tracking | Lifetime |  | years | PCC 2022 | Solar PV tracking | 0.8533 2023: 25; 0.84834 2024: 25; 0.84342 2025: 25; 0.83366 2026: 25; 0.82409 2027: 25
Solar PV tracking | Capital recovery factor |  | % | Calculated | Solar PV tracking | 0.8533 2023: 9.528%; 0.84834 2024: 9.528%; 0.84342 2025: 9.528%; 0.83366 2026: 9.528%; 0.82409 2027: 9.528%
Solar PV tracking | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | Solar PV tracking | 0.8533 2023: 1939.4568; 0.84834 2024: 1846.4332; 0.84342 2025: 1760.2198; 0.83366 2026: 1610.8315; 0.82409 2027: 1472.3105
Solar PV tracking | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | Solar PV tracking | 0.8533 2023: 0.8856; 0.84834 2024: 0.84312; 0.84342 2025: 0.80375; 0.83366 2026: 0.73554; 0.82409 2027: 0.67229
CSP tower 9hrs | Overnight capital cost | 2015 ZAR | ZAR/kW | PCC 2022 | CSP tower 9hrs | 0.8533 2023: 52631; 0.84834 2024: 43999; 0.84342 2025: 35368; 0.83366 2026: 35368; 0.82409 2027: 35368
CSP tower 9hrs | Overnight capital cost | Apr-23 ZAR | ZAR/kW | Calculated | CSP tower 9hrs | 0.8533 2023: 77703.5277; 0.84834 2024: 64959.3873; 0.84342 2025: 52216.7233; 0.83366 2026: 52216.7233; 0.82409 2027: 52216.7233
CSP tower 9hrs | FOM | 2015 ZAR | ZAR/kW/yr | PCC 2022 | CSP tower 9hrs | 0.8533 2023: 1017; 0.84834 2024: 1017; 0.84342 2025: 1017; 0.83366 2026: 1017; 0.82409 2027: 1017
CSP tower 9hrs | FOM | Apr-23 ZAR | ZAR/kW/yr | Calculated | CSP tower 9hrs | 0.8533 2023: 1501.4818; 0.84834 2024: 1501.4818; 0.84342 2025: 1501.4818; 0.83366 2026: 1501.4818; 0.82409 2027: 1501.4818
CSP tower 9hrs | VOM | 2015 ZAR | ZAR/kWh | PCC 2022 | CSP tower 9hrs | 0.8533 2023: 0.00072; 0.84834 2024: 0.00072; 0.84342 2025: 0.00072; 0.83366 2026: 0.00072; 0.82409 2027: 0.00072
CSP tower 9hrs | VOM | Apr-23 ZAR | ZAR/kWh | Calculated | CSP tower 9hrs | 0.8533 2023: 0.001063; 0.84834 2024: 0.001063; 0.84342 2025: 0.001063; 0.83366 2026: 0.001063; 0.82409 2027: 0.001063
CSP tower 9hrs | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | CSP tower 9hrs | 0.8533 2023: 85959.7868; 0.84834 2024: 71861.539; 0.84342 2025: 57764.9244; 0.83366 2026: 57764.9244; 0.82409 2027: 57764.9244
CSP tower 9hrs | Capacity factor | Apr-23 ZAR | % | ERPI 2021 | CSP tower 9hrs | 0.8533 2023: 25%; 0.84834 2024: 25%; 0.84342 2025: 25%; 0.83366 2026: 25%; 0.82409 2027: 25%
CSP tower 9hrs | WACC | Apr-23 ZAR | % | IRP 2023 | CSP tower 9hrs | 0.8533 2023: 8.2%; 0.84834 2024: 8.2%; 0.84342 2025: 8.2%; 0.83366 2026: 8.2%; 0.82409 2027: 8.2%
CSP tower 9hrs | Lifetime |  | years | PCC 2022 | CSP tower 9hrs | 0.8533 2023: 25; 0.84834 2024: 25; 0.84342 2025: 25; 0.83366 2026: 25; 0.82409 2027: 25
CSP tower 9hrs | Capital recovery factor |  | % | Calculated | CSP tower 9hrs | 0.8533 2023: 9.528%; 0.84834 2024: 9.528%; 0.84342 2025: 9.528%; 0.83366 2026: 9.528%; 0.82409 2027: 9.528%
CSP tower 9hrs | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | CSP tower 9hrs | 0.8533 2023: 9692.1034; 0.84834 2024: 8348.7612; 0.84342 2025: 7005.5745; 0.83366 2026: 7005.5745; 0.82409 2027: 7005.5745
CSP tower 9hrs | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | CSP tower 9hrs | 0.8533 2023: 4.4267; 0.84834 2024: 3.8133; 0.84342 2025: 3.2; 0.83366 2026: 3.2; 0.82409 2027: 3.2
Battery storage 4h | Overnight capital cost | 2015 ZAR | ZAR/kW | PCC 2022 | Battery storage 4h | 0.8533 2023: 16510; 0.84834 2024: 11396; 0.84342 2025: 9276; 0.83366 2026: 8116; 0.82409 2027: 6957
Battery storage 4h | Overnight capital cost | Apr-23 ZAR | ZAR/kW | Calculated | Battery storage 4h | 0.8533 2023: 24375.0877; 0.84834 2024: 16824.8637; 0.84342 2025: 13694.9312; 0.83366 2026: 11982.3266; 0.82409 2027: 10271.1984
Battery storage 4h | FOM | 2015 ZAR | ZAR/kW/yr | PCC 2022 | Battery storage 4h | 0.8533 2023: 623; 0.84834 2024: 623; 0.84342 2025: 623; 0.83366 2026: 623; 0.82409 2027: 623
Battery storage 4h | FOM | Apr-23 ZAR | ZAR/kW/yr | Calculated | Battery storage 4h | 0.8533 2023: 919.7868; 0.84834 2024: 919.7868; 0.84342 2025: 919.7868; 0.83366 2026: 919.7868; 0.82409 2027: 919.7868
Battery storage 4h | VOM | 2015 ZAR | ZAR/kWh | PCC 2022 | Battery storage 4h | 0.8533 2023: 0; 0.84834 2024: 0; 0.84342 2025: 0; 0.83366 2026: 0; 0.82409 2027: 0
Battery storage 4h | VOM | Apr-23 ZAR | ZAR/kWh | Calculated | Battery storage 4h | 0.8533 2023: 0; 0.84834 2024: 0; 0.84342 2025: 0; 0.83366 2026: 0; 0.82409 2027: 0
Battery storage 4h | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | Battery storage 4h | 0.8533 2023: 24375.0877; 0.84834 2024: 16824.8637; 0.84342 2025: 13694.9312; 0.83366 2026: 11982.3266; 0.82409 2027: 10271.1984
Battery storage 4h | WACC | Apr-23 ZAR | % | IRP 2023 | Battery storage 4h | 0.8533 2023: 8.2%; 0.84834 2024: 8.2%; 0.84342 2025: 8.2%; 0.83366 2026: 8.2%; 0.82409 2027: 8.2%
Battery storage 4h | Lifetime |  | years | PCC 2022 | Battery storage 4h | 0.8533 2023: 25; 0.84834 2024: 25; 0.84342 2025: 25; 0.83366 2026: 25; 0.82409 2027: 25
Battery storage 4h | Capital recovery factor |  | % | Calculated | Battery storage 4h | 0.8533 2023: 9.528%; 0.84834 2024: 9.528%; 0.84342 2025: 9.528%; 0.83366 2026: 9.528%; 0.82409 2027: 9.528%
Battery storage 4h | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | Battery storage 4h | 0.8533 2023: 3242.3509; 0.84834 2024: 2522.9328; 0.84342 2025: 2224.6993; 0.83366 2026: 2061.5149; 0.82409 2027: 1898.4711
OCGT | Overnight capital cost | 2015 ZAR | ZAR/kW | PCC 2022 | OCGT | 0.8533 2023: 9066; 0.84834 2024: 9066; 0.84342 2025: 9066; 0.83366 2026: 9066; 0.82409 2027: 9066
OCGT | Overnight capital cost | Apr-23 ZAR | ZAR/kW | Calculated | OCGT | 0.8533 2023: 13384.8907; 0.84834 2024: 13384.8907; 0.84342 2025: 13384.8907; 0.83366 2026: 13384.8907; 0.82409 2027: 13384.8907
OCGT | FOM | 2015 ZAR | ZAR/kW/yr | PCC 2022 | OCGT | 0.8533 2023: 162; 0.84834 2024: 162; 0.84342 2025: 162; 0.83366 2026: 162; 0.82409 2027: 162
OCGT | FOM | Apr-23 ZAR | ZAR/kW/yr | Calculated | OCGT | 0.8533 2023: 239.1741; 0.84834 2024: 239.1741; 0.84342 2025: 239.1741; 0.83366 2026: 239.1741; 0.82409 2027: 239.1741
OCGT | VOM | 2015 ZAR | ZAR/kWh | PCC 2022 | OCGT | 0.8533 2023: 0.007; 0.84834 2024: 0.007; 0.84342 2025: 0.007; 0.83366 2026: 0.007; 0.82409 2027: 0.007
OCGT | VOM | Apr-23 ZAR | ZAR/kWh | Calculated | OCGT | 0.8533 2023: 0.010335; 0.84834 2024: 0.010335; 0.84342 2025: 0.010335; 0.83366 2026: 0.010335; 0.82409 2027: 0.010335
OCGT | Heat rate |  | MJ/MWh | PCC 2022 | OCGT | 0.8533 2023: 11613; 0.84834 2024: 11613; 0.84342 2025: 11613; 0.83366 2026: 11613; 0.82409 2027: 11613
OCGT | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | OCGT | 0.8533 2023: 271.95; 0.84834 2024: 271.95; 0.84342 2025: 271.95; 0.83366 2026: 271.95; 0.82409 2027: 271.95
OCGT | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | OCGT | 0.8533 2023: 3.1582; 0.84834 2024: 3.1582; 0.84342 2025: 3.1582; 0.83366 2026: 3.1582; 0.82409 2027: 3.1582
OCGT | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | OCGT | 0.8533 2023: 14372.6956; 0.84834 2024: 14372.6956; 0.84342 2025: 14372.6956; 0.83366 2026: 14372.6956; 0.82409 2027: 14372.6956
OCGT | Capacity factor | Apr-23 ZAR | % | ERPI 2021 | OCGT | 0.8533 2023: 10%; 0.84834 2024: 10%; 0.84342 2025: 10%; 0.83366 2026: 10%; 0.82409 2027: 10%
OCGT | WACC | Apr-23 ZAR | % | IRP 2023 | OCGT | 0.8533 2023: 8.2%; 0.84834 2024: 8.2%; 0.84342 2025: 8.2%; 0.83366 2026: 8.2%; 0.82409 2027: 8.2%
OCGT | Lifetime |  | years | PCC 2022 | OCGT | 0.8533 2023: 25; 0.84834 2024: 25; 0.84342 2025: 25; 0.83366 2026: 25; 0.82409 2027: 25
OCGT | Capital recovery factor |  | % | Calculated | OCGT | 0.8533 2023: 9.528%; 0.84834 2024: 9.528%; 0.84342 2025: 9.528%; 0.83366 2026: 9.528%; 0.82409 2027: 9.528%
OCGT | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | OCGT | 0.8533 2023: 1608.6669; 0.84834 2024: 1608.6669; 0.84342 2025: 1608.6669; 0.83366 2026: 1608.6669; 0.82409 2027: 1608.6669
OCGT | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | OCGT | 0.8533 2023: 5.0049; 0.84834 2024: 5.0049; 0.84342 2025: 5.0049; 0.83366 2026: 5.0049; 0.82409 2027: 5.0049
ICE | Overnight capital cost | 2015 ZAR | ZAR/kW | PCC 2022 | ICE | 0.8533 2023: 14144; 0.84834 2024: 14144; 0.84342 2025: 14144; 0.83366 2026: 14144; 0.82409 2027: 14144
ICE | Overnight capital cost | Apr-23 ZAR | ZAR/kW | Calculated | ICE | 0.8533 2023: 20881.9649; 0.84834 2024: 20881.9649; 0.84342 2025: 20881.9649; 0.83366 2026: 20881.9649; 0.82409 2027: 20881.9649
ICE | FOM | 2015 ZAR | ZAR/kW/yr | PCC 2022 | ICE | 0.8533 2023: 425; 0.84834 2024: 425; 0.84342 2025: 425; 0.83366 2026: 425; 0.82409 2027: 425
ICE | FOM | Apr-23 ZAR | ZAR/kW/yr | Calculated | ICE | 0.8533 2023: 627.4629; 0.84834 2024: 627.4629; 0.84342 2025: 627.4629; 0.83366 2026: 627.4629; 0.82409 2027: 627.4629
ICE | VOM | 2015 ZAR | ZAR/kWh | PCC 2022 | ICE | 0.8533 2023: 0.07056; 0.84834 2024: 0.07056; 0.84342 2025: 0.07056; 0.83366 2026: 0.07056; 0.82409 2027: 0.07056
ICE | VOM | Apr-23 ZAR | ZAR/kWh | Calculated | ICE | 0.8533 2023: 0.10417; 0.84834 2024: 0.10417; 0.84342 2025: 0.10417; 0.83366 2026: 0.10417; 0.82409 2027: 0.10417
ICE | Heat rate |  | MJ/MWh | PCC 2022 | ICE | 0.8533 2023: 8000; 0.84834 2024: 8000; 0.84342 2025: 8000; 0.83366 2026: 8000; 0.82409 2027: 8000
ICE | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | ICE | 0.8533 2023: 271.95; 0.84834 2024: 271.95; 0.84342 2025: 271.95; 0.83366 2026: 271.95; 0.82409 2027: 271.95
ICE | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | ICE | 0.8533 2023: 2.1756; 0.84834 2024: 2.1756; 0.84342 2025: 2.1756; 0.83366 2026: 2.1756; 0.82409 2027: 2.1756
ICE | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | ICE | 0.8533 2023: 23164.1465; 0.84834 2024: 23164.1465; 0.84342 2025: 23164.1465; 0.83366 2026: 23164.1465; 0.82409 2027: 23164.1465
ICE | Capacity factor | Apr-23 ZAR | % | ERPI 2021 | ICE | 0.8533 2023: 10%; 0.84834 2024: 10%; 0.84342 2025: 10%; 0.83366 2026: 10%; 0.82409 2027: 10%
ICE | WACC | Apr-23 ZAR | % | IRP 2023 | ICE | 0.8533 2023: 8.2%; 0.84834 2024: 8.2%; 0.84342 2025: 8.2%; 0.83366 2026: 8.2%; 0.82409 2027: 8.2%
ICE | Lifetime |  | years | PCC 2022 | ICE | 0.8533 2023: 25; 0.84834 2024: 25; 0.84342 2025: 25; 0.83366 2026: 25; 0.82409 2027: 25
ICE | Capital recovery factor |  | % | Calculated | ICE | 0.8533 2023: 9.528%; 0.84834 2024: 9.528%; 0.84342 2025: 9.528%; 0.83366 2026: 9.528%; 0.82409 2027: 9.528%
ICE | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | ICE | 0.8533 2023: 2834.6433; 0.84834 2024: 2834.6433; 0.84342 2025: 2834.6433; 0.83366 2026: 2834.6433; 0.82409 2027: 2834.6433
ICE | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | ICE | 0.8533 2023: 5.5157; 0.84834 2024: 5.5157; 0.84342 2025: 5.5157; 0.83366 2026: 5.5157; 0.82409 2027: 5.5157
CCGT | Overnight capital cost | 2015 ZAR | ZAR/kW | PCC 2022 | CCGT | 0.8533 2023: 9955; 0.84834 2024: 9955; 0.84342 2025: 9955; 0.83366 2026: 9955; 0.82409 2027: 9955
CCGT | Overnight capital cost | Apr-23 ZAR | ZAR/kW | Calculated | CCGT | 0.8533 2023: 14697.3954; 0.84834 2024: 14697.3954; 0.84342 2025: 14697.3954; 0.83366 2026: 14697.3954; 0.82409 2027: 14697.3954
CCGT | FOM | 2015 ZAR | ZAR/kW/yr | PCC 2022 | CCGT | 0.8533 2023: 167; 0.84834 2024: 167; 0.84342 2025: 167; 0.83366 2026: 167; 0.82409 2027: 167
CCGT | FOM | Apr-23 ZAR | ZAR/kW/yr | Calculated | CCGT | 0.8533 2023: 246.556; 0.84834 2024: 246.556; 0.84342 2025: 246.556; 0.83366 2026: 246.556; 0.82409 2027: 246.556
CCGT | VOM | 2015 ZAR | ZAR/kWh | PCC 2022 | CCGT | 0.8533 2023: 0.02196; 0.84834 2024: 0.02196; 0.84342 2025: 0.02196; 0.83366 2026: 0.02196; 0.82409 2027: 0.02196
CCGT | VOM | Apr-23 ZAR | ZAR/kWh | Calculated | CCGT | 0.8533 2023: 0.032421; 0.84834 2024: 0.032421; 0.84342 2025: 0.032421; 0.83366 2026: 0.032421; 0.82409 2027: 0.032421
CCGT | Heat rate |  | MJ/MWh | PCC 2022 | CCGT | 0.8533 2023: 7436.9; 0.84834 2024: 7436.9; 0.84342 2025: 7436.9; 0.83366 2026: 7436.9; 0.82409 2027: 7436.9
CCGT | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | CCGT | 0.8533 2023: 271.95; 0.84834 2024: 271.95; 0.84342 2025: 271.95; 0.83366 2026: 271.95; 0.82409 2027: 271.95
CCGT | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | CCGT | 0.8533 2023: 2.0225; 0.84834 2024: 2.0225; 0.84342 2025: 2.0225; 0.83366 2026: 2.0225; 0.82409 2027: 2.0225
CCGT | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | CCGT | 0.8533 2023: 16303.6679; 0.84834 2024: 16303.6679; 0.84342 2025: 16303.6679; 0.83366 2026: 16303.6679; 0.82409 2027: 16303.6679
CCGT | Capacity factor | Apr-23 ZAR | % | ERPI 2021 | CCGT | 0.8533 2023: 50%; 0.84834 2024: 50%; 0.84342 2025: 50%; 0.83366 2026: 50%; 0.82409 2027: 50%
CCGT | WACC | Apr-23 ZAR | % | IRP 2023 | CCGT | 0.8533 2023: 8.2%; 0.84834 2024: 8.2%; 0.84342 2025: 8.2%; 0.83366 2026: 8.2%; 0.82409 2027: 8.2%
CCGT | Lifetime |  | years | PCC 2022 | CCGT | 0.8533 2023: 25; 0.84834 2024: 25; 0.84342 2025: 25; 0.83366 2026: 25; 0.82409 2027: 25
CCGT | Capital recovery factor |  | % | Calculated | CCGT | 0.8533 2023: 9.528%; 0.84834 2024: 9.528%; 0.84342 2025: 9.528%; 0.83366 2026: 9.528%; 0.82409 2027: 9.528%
CCGT | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | CCGT | 0.8533 2023: 1800.0403; 0.84834 2024: 1800.0403; 0.84342 2025: 1800.0403; 0.83366 2026: 1800.0403; 0.82409 2027: 1800.0403
CCGT | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | CCGT | 0.8533 2023: 2.4659; 0.84834 2024: 2.4659; 0.84342 2025: 2.4659; 0.83366 2026: 2.4659; 0.82409 2027: 2.4659
Nuclear | Overnight capital cost | 2015 ZAR | ZAR/kW | PCC 2022 | Nuclear | 0.8533 2023: 68550; 0.84834 2024: 68550; 0.84342 2025: 68550; 0.83366 2026: 68550; 0.82409 2027: 68550
Nuclear | Overnight capital cost | Apr-23 ZAR | ZAR/kW | Calculated | Nuclear | 0.8533 2023: 101206.0729; 0.84834 2024: 101206.0729; 0.84342 2025: 101206.0729; 0.83366 2026: 101206.0729; 0.82409 2027: 101206.0729
Nuclear | FOM | 2015 ZAR | ZAR/kW/yr | PCC 2022 | Nuclear | 0.8533 2023: 977; 0.84834 2024: 977; 0.84342 2025: 977; 0.83366 2026: 977; 0.82409 2027: 977
Nuclear | FOM | Apr-23 ZAR | ZAR/kW/yr | Calculated | Nuclear | 0.8533 2023: 1442.4265; 0.84834 2024: 1442.4265; 0.84342 2025: 1442.4265; 0.83366 2026: 1442.4265; 0.82409 2027: 1442.4265
Nuclear | VOM | 2015 ZAR | ZAR/kWh | PCC 2022 | Nuclear | 0.8533 2023: 0.01; 0.84834 2024: 0.01; 0.84342 2025: 0.01; 0.83366 2026: 0.01; 0.82409 2027: 0.01
Nuclear | VOM | Apr-23 ZAR | ZAR/kWh | Calculated | Nuclear | 0.8533 2023: 0.014764; 0.84834 2024: 0.014764; 0.84342 2025: 0.014764; 0.83366 2026: 0.014764; 0.82409 2027: 0.014764
Nuclear | Heat rate |  | MJ/MWh | PCC 2022 | Nuclear | 0.8533 2023: 10285.7; 0.84834 2024: 10285.7; 0.84342 2025: 10285.7; 0.83366 2026: 10285.7; 0.82409 2027: 10285.7
Nuclear | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | Nuclear | 0.8533 2023: 14.22; 0.84834 2024: 14.22; 0.84342 2025: 14.22; 0.83366 2026: 14.22; 0.82409 2027: 14.22
Nuclear | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | Nuclear | 0.8533 2023: 0.14626; 0.84834 2024: 0.14626; 0.84342 2025: 0.14626; 0.83366 2026: 0.14626; 0.82409 2027: 0.14626
Nuclear | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | Nuclear | 0.8533 2023: 126062.1388; 0.84834 2024: 126062.1388; 0.84342 2025: 126062.1388; 0.83366 2026: 126062.1388; 0.82409 2027: 126062.1388
Nuclear | Capacity factor | Apr-23 ZAR | % | ERPI 2021 | Nuclear | 0.8533 2023: 85%; 0.84834 2024: 85%; 0.84342 2025: 85%; 0.83366 2026: 85%; 0.82409 2027: 85%
Nuclear | WACC | Apr-23 ZAR | % | IRP 2023 | Nuclear | 0.8533 2023: 8.2%; 0.84834 2024: 8.2%; 0.84342 2025: 8.2%; 0.83366 2026: 8.2%; 0.82409 2027: 8.2%
Nuclear | Lifetime |  | years | PCC 2022 | Nuclear | 0.8533 2023: 25; 0.84834 2024: 25; 0.84342 2025: 25; 0.83366 2026: 25; 0.82409 2027: 25
Nuclear | Capital recovery factor |  | % | Calculated | Nuclear | 0.8533 2023: 9.528%; 0.84834 2024: 9.528%; 0.84342 2025: 9.528%; 0.83366 2026: 9.528%; 0.82409 2027: 9.528%
Nuclear | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | Nuclear | 0.8533 2023: 13454.1743; 0.84834 2024: 13454.1743; 0.84342 2025: 13454.1743; 0.83366 2026: 13454.1743; 0.82409 2027: 13454.1743
Nuclear | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | Nuclear | 0.8533 2023: 1.9679; 0.84834 2024: 1.9679; 0.84342 2025: 1.9679; 0.83366 2026: 1.9679; 0.82409 2027: 1.9679
Coal - no CCS -1 | Overnight capital cost | 2015 ZAR | ZAR/kW | PCC 2022 | Coal PF -no CCS | 0.8533 2023: 39335; 0.84834 2024: 39335; 0.84342 2025: 39335; 0.83366 2026: 39335; 0.82409 2027: 39335
Coal - no CCS -1 | Overnight capital cost | Apr-23 ZAR | ZAR/kW | Calculated | Coal PF -no CCS | 0.8533 2023: 58073.5358; 0.84834 2024: 58073.5358; 0.84342 2025: 58073.5358; 0.83366 2026: 58073.5358; 0.82409 2027: 58073.5358
Coal - no CCS -1 | FOM | 2015 ZAR | ZAR/kW/yr | PCC 2022 | Coal PF -no CCS | 0.8533 2023: 933; 0.84834 2024: 933; 0.84342 2025: 933; 0.83366 2026: 933; 0.82409 2027: 933
Coal - no CCS -1 | FOM | Apr-23 ZAR | ZAR/kW/yr | Calculated | Coal PF -no CCS | 0.8533 2023: 1377.4656; 0.84834 2024: 1377.4656; 0.84342 2025: 1377.4656; 0.83366 2026: 1377.4656; 0.82409 2027: 1377.4656
Coal - no CCS -1 | VOM | 2015 ZAR | ZAR/kWh | PCC 2022 | Coal PF -no CCS | 0.8533 2023: 0.022; 0.84834 2024: 0.022; 0.84342 2025: 0.022; 0.83366 2026: 0.022; 0.82409 2027: 0.022
Coal - no CCS -1 | VOM | Apr-23 ZAR | ZAR/kWh | Calculated | Coal PF -no CCS | 0.8533 2023: 0.03248; 0.84834 2024: 0.03248; 0.84342 2025: 0.03248; 0.83366 2026: 0.03248; 0.82409 2027: 0.03248
Coal - no CCS -1 | Heat rate |  | MJ/MWh | PCC 2022 | Coal PF -no CCS | 0.8533 2023: 8181.8; 0.84834 2024: 8181.8; 0.84342 2025: 8181.8; 0.83366 2026: 8181.8; 0.82409 2027: 8181.8
Coal - no CCS -1 | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | Coal PF -no CCS | 0.8533 2023: 45.18; 0.84834 2024: 45.18; 0.84342 2025: 45.18; 0.83366 2026: 45.18; 0.82409 2027: 45.18
Coal - no CCS -1 | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | Coal PF -no CCS | 0.8533 2023: 0.36965; 0.84834 2024: 0.36965; 0.84342 2025: 0.36965; 0.83366 2026: 0.36965; 0.82409 2027: 0.36965
Coal - no CCS -1 | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | Coal PF -no CCS | 0.8533 2023: 64402.0695; 0.84834 2024: 64402.0695; 0.84342 2025: 64402.0695; 0.83366 2026: 64402.0695; 0.82409 2027: 64402.0695
Coal - no CCS -1 | Capacity factor | Apr-23 ZAR | % | ERPI 2021 | Coal PF -no CCS | 0.8533 2023: 85%; 0.84834 2024: 85%; 0.84342 2025: 85%; 0.83366 2026: 85%; 0.82409 2027: 85%
Coal - no CCS -1 | WACC | Apr-23 ZAR | % | IRP 2023 | Coal PF -no CCS | 0.8533 2023: 8.2%; 0.84834 2024: 8.2%; 0.84342 2025: 8.2%; 0.83366 2026: 8.2%; 0.82409 2027: 8.2%
Coal - no CCS -1 | Lifetime |  | years | PCC 2022 | Coal PF -no CCS | 0.8533 2023: 25; 0.84834 2024: 25; 0.84342 2025: 25; 0.83366 2026: 25; 0.82409 2027: 25
Coal - no CCS -1 | Capital recovery factor |  | % | Calculated | Coal PF -no CCS | 0.8533 2023: 9.528%; 0.84834 2024: 9.528%; 0.84342 2025: 9.528%; 0.83366 2026: 9.528%; 0.82409 2027: 9.528%
Coal - no CCS -1 | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | Coal PF -no CCS | 0.8533 2023: 7513.9743; 0.84834 2024: 7513.9743; 0.84342 2025: 7513.9743; 0.83366 2026: 7513.9743; 0.82409 2027: 7513.9743
Coal - no CCS -1 | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | Coal PF -no CCS | 0.8533 2023: 1.4113; 0.84834 2024: 1.4113; 0.84342 2025: 1.4113; 0.83366 2026: 1.4113; 0.82409 2027: 1.4113
Coal - no CCS -2 | Overnight capital cost | 2015 ZAR | ZAR/kW | PCC 2022 | Coal FBC - no CCS | 0.8533 2023: 47478; 0.84834 2024: 47478; 0.84342 2025: 47478; 0.83366 2026: 47478; 0.82409 2027: 47478
Coal - no CCS -2 | Overnight capital cost | Apr-23 ZAR | ZAR/kW | Calculated | Coal FBC - no CCS | 0.8533 2023: 70095.7247; 0.84834 2024: 70095.7247; 0.84342 2025: 70095.7247; 0.83366 2026: 70095.7247; 0.82409 2027: 70095.7247
Coal - no CCS -2 | FOM | 2015 ZAR | ZAR/kW/yr | PCC 2022 | Coal FBC - no CCS | 0.8533 2023: 627; 0.84834 2024: 627; 0.84342 2025: 627; 0.83366 2026: 627; 0.82409 2027: 627
Coal - no CCS -2 | FOM | Apr-23 ZAR | ZAR/kW/yr | Calculated | Coal FBC - no CCS | 0.8533 2023: 925.6923; 0.84834 2024: 925.6923; 0.84342 2025: 925.6923; 0.83366 2026: 925.6923; 0.82409 2027: 925.6923
Coal - no CCS -2 | VOM | 2015 ZAR | ZAR/kWh | PCC 2022 | Coal FBC - no CCS | 0.8533 2023: 0.08064; 0.84834 2024: 0.08064; 0.84342 2025: 0.08064; 0.83366 2026: 0.08064; 0.82409 2027: 0.08064
Coal - no CCS -2 | VOM | Apr-23 ZAR | ZAR/kWh | Calculated | Coal FBC - no CCS | 0.8533 2023: 0.11906; 0.84834 2024: 0.11906; 0.84342 2025: 0.11906; 0.83366 2026: 0.11906; 0.82409 2027: 0.11906
Coal - no CCS -2 | Heat rate |  | MJ/MWh | PCC 2022 | Coal FBC - no CCS | 0.8533 2023: 10909; 0.84834 2024: 10909; 0.84342 2025: 10909; 0.83366 2026: 10909; 0.82409 2027: 10909
Coal - no CCS -2 | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | Coal FBC - no CCS | 0.8533 2023: 45.18; 0.84834 2024: 45.18; 0.84342 2025: 45.18; 0.83366 2026: 45.18; 0.82409 2027: 45.18
Coal - no CCS -2 | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | Coal FBC - no CCS | 0.8533 2023: 0.49287; 0.84834 2024: 0.49287; 0.84342 2025: 0.49287; 0.83366 2026: 0.49287; 0.82409 2027: 0.49287
Coal - no CCS -2 | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | Coal FBC - no CCS | 0.8533 2023: 77734.3703; 0.84834 2024: 77734.3703; 0.84342 2025: 77734.3703; 0.83366 2026: 77734.3703; 0.82409 2027: 77734.3703
Coal - no CCS -2 | Capacity factor | Apr-23 ZAR | % | ERPI 2021 | Coal FBC - no CCS | 0.8533 2023: 85%; 0.84834 2024: 85%; 0.84342 2025: 85%; 0.83366 2026: 85%; 0.82409 2027: 85%
Coal - no CCS -2 | WACC | Apr-23 ZAR | % | IRP 2023 | Coal FBC - no CCS | 0.8533 2023: 8.2%; 0.84834 2024: 8.2%; 0.84342 2025: 8.2%; 0.83366 2026: 8.2%; 0.82409 2027: 8.2%
Coal - no CCS -2 | Lifetime |  | years | PCC 2022 | Coal FBC - no CCS | 0.8533 2023: 25; 0.84834 2024: 25; 0.84342 2025: 25; 0.83366 2026: 25; 0.82409 2027: 25
Coal - no CCS -2 | Capital recovery factor |  | % | Calculated | Coal FBC - no CCS | 0.8533 2023: 9.528%; 0.84834 2024: 9.528%; 0.84342 2025: 9.528%; 0.83366 2026: 9.528%; 0.82409 2027: 9.528%
Coal - no CCS -2 | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | Coal FBC - no CCS | 0.8533 2023: 8332.5606; 0.84834 2024: 8332.5606; 0.84342 2025: 8332.5606; 0.83366 2026: 8332.5606; 0.82409 2027: 8332.5606
Coal - no CCS -2 | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | Coal FBC - no CCS | 0.8533 2023: 1.731; 0.84834 2024: 1.731; 0.84342 2025: 1.731; 0.83366 2026: 1.731; 0.82409 2027: 1.731
Coal - CCS | Overnight capital cost | 2015 ZAR | ZAR/kW | PCC 2022 | Coal with CCS | 0.8533 2023: 76087; 0.84834 2024: 76087; 0.84342 2025: 76087; 0.83366 2026: 76087; 0.82409 2027: 76087
Coal - CCS | Overnight capital cost | Apr-23 ZAR | ZAR/kW | Calculated | Coal with CCS | 0.8533 2023: 112333.5735; 0.84834 2024: 112333.5735; 0.84342 2025: 112333.5735; 0.83366 2026: 112333.5735; 0.82409 2027: 112333.5735
Coal - CCS | FOM | 2015 ZAR | ZAR/kW/yr | PCC 2022 | Coal with CCS | 0.8533 2023: 1590; 0.84834 2024: 1590; 0.84342 2025: 1590; 0.83366 2026: 1590; 0.82409 2027: 1590
Coal - CCS | FOM | Apr-23 ZAR | ZAR/kW/yr | Calculated | Coal with CCS | 0.8533 2023: 2347.4494; 0.84834 2024: 2347.4494; 0.84342 2025: 2347.4494; 0.83366 2026: 2347.4494; 0.82409 2027: 2347.4494
Coal - CCS | VOM | 2015 ZAR | ZAR/kWh | PCC 2022 | Coal with CCS | 0.8533 2023: 0.041; 0.84834 2024: 0.041; 0.84342 2025: 0.041; 0.83366 2026: 0.041; 0.82409 2027: 0.041
Coal - CCS | VOM | Apr-23 ZAR | ZAR/kWh | Calculated | Coal with CCS | 0.8533 2023: 0.060532; 0.84834 2024: 0.060532; 0.84342 2025: 0.060532; 0.83366 2026: 0.060532; 0.82409 2027: 0.060532
Coal - CCS | Heat rate |  | MJ/MWh | PCC 2022 | Coal with CCS | 0.8533 2023: 10909; 0.84834 2024: 10909; 0.84342 2025: 10909; 0.83366 2026: 10909; 0.82409 2027: 10909
Coal - CCS | Fuel (before conversion) | Apr-23 ZAR | ZAR/GJ | IRP 2023 | Coal with CCS | 0.8533 2023: 45.18; 0.84834 2024: 45.18; 0.84342 2025: 45.18; 0.83366 2026: 45.18; 0.82409 2027: 45.18
Coal - CCS | Fuel (after efficiency) | Apr-23 ZAR | ZAR/kWh | IRP 2023 | Coal with CCS | 0.8533 2023: 0.49287; 0.84834 2024: 0.49287; 0.84342 2025: 0.49287; 0.83366 2026: 0.49287; 0.82409 2027: 0.49287
Coal - CCS | Total capital cost | Apr-23 ZAR | ZAR/kW | Calculated | Coal with CCS | 0.8533 2023: 124575.067; 0.84834 2024: 124575.067; 0.84342 2025: 124575.067; 0.83366 2026: 124575.067; 0.82409 2027: 124575.067
Coal - CCS | Capacity factor | Apr-23 ZAR | % | ERPI 2021 | Coal with CCS | 0.8533 2023: 85%; 0.84834 2024: 85%; 0.84342 2025: 85%; 0.83366 2026: 85%; 0.82409 2027: 85%
Coal - CCS | WACC | Apr-23 ZAR | % | IRP 2023 | Coal with CCS | 0.8533 2023: 8.2%; 0.84834 2024: 8.2%; 0.84342 2025: 8.2%; 0.83366 2026: 8.2%; 0.82409 2027: 8.2%
Coal - CCS | Lifetime |  | years | PCC 2022 | Coal with CCS | 0.8533 2023: 25; 0.84834 2024: 25; 0.84342 2025: 25; 0.83366 2026: 25; 0.82409 2027: 25
Coal - CCS | Capital recovery factor |  | % | Calculated | Coal with CCS | 0.8533 2023: 9.528%; 0.84834 2024: 9.528%; 0.84342 2025: 9.528%; 0.83366 2026: 9.528%; 0.82409 2027: 9.528%
Coal - CCS | Annualised cost | Apr-23 ZAR | ZAR/kW/yr | Calculated | Coal with CCS | 0.8533 2023: 14217.5026; 0.84834 2024: 14217.5026; 0.84342 2025: 14217.5026; 0.83366 2026: 14217.5026; 0.82409 2027: 14217.5026
Coal - CCS | LCOE | Apr-23 ZAR | ZAR/kWh | Calculated | Coal with CCS | 0.8533 2023: 2.4628; 0.84834 2024: 2.4628; 0.84342 2025: 2.4628; 0.83366 2026: 2.4628; 0.82409 2027: 2.4628

## Assumptions Distrubution
Assumptions Electricity Distribution
The distribution technologies capture the average losses incurred by each sector. Currently all sectors are modelled to experience electricity supply at national average distribution losses (10%). Large industries may however have their own proximate substation supplied at the very highest distribution voltage so losses would be lower than is currently modelled in SATIM. This is in the process of being amended.
The capacity is set according to the peak demand in each sector plus the reserve margin.
A reserve constraint is imposed on each distribution technology to ensure the reserve is maintained.
The operating cost of the distribution technology is set to reflect the average tariff seen by each sector.
The investment cost of new distribution capacity is set to reflect average cost of investment.

## Assumptions Generation
Existing Power Plants
Parameter | Description | Data + Sources | Additional Assumptions for New Power Plants:
Energy Input Commodity or Fuel | Fuel is coal, diesel and other fuels | Annex A1 | There is no initial capacity or retirement profile for new technologies but future capacity is bounded by a capacity limit parameter.
Output Commodity | In this case is centralized electricity (ELCC). | Annex A1 | An investment cost is specified. Renewable technologies have investment costs that decrease over time to capture the effect of learning from global installed capacity (note that in this model this parameter is set exogenously).
Efficiency | Relates the energy input commodities to the sum of energy output commodities. | Annex A3 | A technology lead-time is specified to capture the construction duration.
Fixed and Variable operating and maintenance cost | Relates to yearly cost to run power technologies. Excludes fuel costs except in the case of the Koeberg nuclear plant. | Annex A3 | In the case of committed build, a lower bound is imposed on the new capacity as per the build plan, taking into account the construction duration.
Overnight Investment Cost | Cost of construction for a technology, assuming that the facility is built and commissioned instantaneously | Annex A3 | Some technologies have a lower bound on the load factor (also called capacity factor) to characterize fuel contracts. This is defined by setting up an inequality relationship between special algebraic parameters rather than the parameter-value/s pair method of most other parameterisation in TIMES. This means that the plants must generate a minimum of electricity to attain this capacity factor. Currently in SATIM this only applies to gas-fuelled gas turbine plant which must maintain a load factor in excess of 20% in terms of fuel supply contracts.
Annual Availability | Refers to the percentage of time within a year that a power generation facility is capable of producing electricity under normal operating conditions. Accounting for scheduled and unplanned downtime. | Annex A3 | SATIM has two wind classes, with capacity factors of 29% and 25%,to reflect the varying quality of sites. Each wind class is bounded by the potential for deployment in each class, that is, the minimum or maximum limit on capacity built specifically in that year. Currently in SATIM this is only used to reflect historical build of the high resource wind class .
Refurbishment/retirement profile | Specifies the capacity that is initially available and how that increases in the case of refurbishments and decreases as plants or parts of plants retire in the future. The assumed profiles for Eskom plants are described below. | Annex A3 | The intermittency of wind is captured by setting the capacity availability equal to the energy availability. For instance a 100 MW wind farm at 29% estimated capacity factor will be modelled as only being able to produce 29MW of output in any time-slice.
Lifetime | Refers to operational life of a technology, | Annex A3 | The capacity credit of wind is fixed at a conservative value below the capacity factor. Currently in SATIM the capacity credit for both wind classes is set to 0.23.
In SATIM, solar PV without battery storage can only output power during daytime hours. This is accomplished by setting the capacity factor per time slice. Timeslices not in daylight are set to zero.
Additional Parameterization for Combined Heat & Power (CHP) Plants
Parameter | Description
Industrial Process Heat [IPPS] | CHP’s are modelled as producing a second output commodity, Industrial Process Heat [IPPS] pertaining to the sub-sector (eg. Iron & Steel) in which the CHP is found.
Operating in back-pressure, with a constant Electricity to Heat output ratio [NCAP_CHPR]. | In back pressure mode you cannot bypass the heat load so the electricity to heat ratio is constant. Alternatively in ‘Condensing’ mode, the electricity to heat ratio is determined endogenously which requires a number of additional parameters and is appropriate when CHP has a large share of the system which is not the case in SATIM.
Additional input fuel | Some CHP’s are given the option to use an alternate fuel (e.g. biomass and coal). The share of biomass/coal is fixed based on estimates of historical consumption.
Additional Parameterization for Existing Pump Storage Systems
Parameter | Description
Night storage technology [NST] | In TIMES you need to declare storage technologies as such and the storage dam technology is allocated as a member of the set [NST] which signifies it as a night storage technology.
Parameter Attribution | The cycle efficiency of the system is attributed to the pump technology. The capacity and cost parameters are attributed to the turbine.
Input + Output commodity | The input commodity is electricity downstream of transmission (ELC), and the output commodity is electricity upstream of transmission (ELCC).

## Assumptions Transmission
Assumptions Electricity Transmission
Transmission of electricity between ELCC and the MV distribution network incurs a loss of 3.9%.
MV electricity is distributed to each sector in a way that captures the different levels of losses that are incurred distributing electricity to the sector. For example,the distribution of electricity to residential households is assumed to incur a loss of 19.7% whereas the distribution of electricity to the industrial sectors (excluding mining) incurs a smaller average loss of 6.%.
An existing stock/capacity for the transmission technology is estimated based on the peak demand in the base year plus a reserve margin. For the base year of 2006, this is currently estimated as 31.8 GW.
The operating cost of is set to reflect the estimated running cost of this Infrastructure. Currently estimated as 287.91 R/kW.
The investment cost of new transmission capacity is set to reflect estimated average cost of investment. Currently estimated at 6329.31 R/kW.
A reserve constraint is imposed on ELC to ensure the reserve is maintained.

## Deflator Assumptions
South Africa |  |  | Comments |  | IRP Fuel costs |  | ZAR/GJ
Date | CPI |  |  |  | 2023-04-01 | Natural gas | 271.95
2011-11-01 | 61 |  |  |  | 2023-04-01 | Coal | 45.18
2012-03-01 | 62.5 |  |  |  | 2023-04-01 | Nuclear -1 | 14.22
2013-08-01 | 67.3 |  |  |  | 2023-04-01 | Nuclear -2 | 17.93
2014-08-01 | 71.7 |  |  |  | 2023-04-01 | Biomass | 10 | Assumption
2015-11-01 | 75.2 |  |  |  | 2023-04-01 | Forestry residue | 43.3
2015-12-01 | 75.4
Average 2015 | 74.1
2016-04-01 | 78.3
2019-01-01 | 87.9 |  |  | IRP adj from EPRI Jan 2021 ZAR to Apr 2023 ZAR
2020-12-01 | 94.4 |  |  | 1.2058
Average 2020 | 93.3
2021-06-01 | 97
2022-10-01 | 106.5
2022-12-01 | 107.2
2023-01-01 | 107.1 |  | 2015 ZAR -> Apr 2023 ZAR
2023-04-01 | 109.4 |  | 1.4764
2023-11-01 | 112.7
2023-12-01 | 112.7
2024-01-01 | 112.7 |  | assumed
Sources:
Exchange rates |  | https://www.nedbank.co.za/content/dam/nedbank/site-assets/AboutUs/Economics_Unit/Forecast_and_data/Daily_Rates/Monthly_Average_Exchange_Rates.pdf
South Africa CPI |  | https://www.statssa.gov.za/publications/P0141/CPIHistory.pdf